## Schedule 2A SS_Ganjam
ORISSA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2X12.5MVA 132/33KV Sub-Stations Renovation work at GANJAM with associated works.
Bid Document No. : Sr. G.M-CPC-TENDER-PACKAGE- 66-01 /2011
(Equipment/Materials Price Break-up of Ex-works Prices against PACKAGE GANJAM )
Bidder's Name & Address: |  | To,
Orissa Power Transmission Corporation Ltd.,Bhubneshwar
| PART-I, SCHEDULE-2A (FOR SUBSTATION) |  |  |  | PRICE IN INDIAN RUPEES
SL NO | SUPPLY OF FOLLOWING EQUIPMENTS (As per Technical Specification) | Unit |  | Quantity for 2X12.5 MVA 132/33kV Substation Renovation works at Ganjam (132 KV Feeder Bay:01 No.,132 KV Transformer Bay:02 Nos,33 KV Transformer Bay: 02 Nos, 33 KV Feeder Bay:03 Nos, 33 KV Bus Coupler Bay:01 No.). | Unit Ex-works Price | Total Ex-works Price | Mode of Transaction (Direct or Bought-out item) | Total Taxes & Duties applicable for transaction between bidder and OPTCL and not included in the price at Column(6) [For bought-out items, taxes & duties excluding Octroi/Entry Tax are invariably included in the price quoted at column(6)]
[8 empty] | Excise Duty | Sales Tax | Other Levies(if any)
1 | 2 | 3 | 0 | 4 | 5 | 6=4X5 | 7 | 8 | 9 | 10
1 | 145 KV,800-400-200/1-1-1-1 A,40 KA,4CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 9
2 | 145 KV,1200A,40 KA,ISOLATORS
2.1 | S/I WITH OUT EARTH SWITCH | NOS |  | 6
2.2 | D/I WITH SINGLE EARTH SWITCH | NOS |  | 1
3 | 145 KV,6600pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS |  | 3
4 | 120 KV METAL OXIDE SURGE ARRESTOR, 10 KA, Class III | NOS |  | 9
6 | 132 KV Bus Post Insulators | NOS |  | 5
7 | 145KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 3
8 | 36 KV,(800-400-200/1-1-1 A),25KA,3CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 15
9 | 36 KV Class NCT FOR TRANSFORMER PROTECTION RATING (800-400-200/1-1 A)( IN EACH POWER TRANSFORMER 132 KV SIDE-1 NO) | NOS |  | 2
10 | 36 KV Class NCT FOR TRANSFORMER PROTECTION RATING (800-400-200/1-1 A)( IN EACH POWER TRANSFORMER 33 KV SIDE 1 No.) | NOS |  | 2
11 | 30 KV, METAL OXIDE SURGE ARRESTOR, 10KA, class II | NOS |  | 6
12 | 36 KV ,2 CORE,SINGLE PHASE,IVT | NOS |  | 3
13 | 36KV,1250A,25KA,VACUUM CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 2
14 | 33 KV Bus Post Insulators | NOS |  | 6
15 | BUS BAR & CIRCUIT MATERIALS( all insulators as indicated below shall be of “LONG ROD ” Type
15.1 | 120 KN INSULATOR STRINGS(TENSION for single ACSR Moose)-132 KV | SET |  | 18
15.2 | 120 KN INSULATOR STRINGS(TENSION for Single ACSR Moose)-33 KV | SET |  | 9
15.3 | 120 KN INSULATOR STRINGS (SUSPENSION for single ACSR Moose)-132 KV | SET |  | 12
15.4 | 120 KN INSULATOR STRINGS (SUSPENSION for Single ACSR Moose)-33 KV | SET |  | 9
16 | ACSR MOOSE CONDUCTOR | KM |  | 0.5
17 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | LOT |  | 1
18 | SUBSTATION SYSTEMS
18.1 | EARTHING CONDUCTOR (75x10mm for laying (spacing maximum 5m) (GI FLAT) | LOT |  | 1
18.2 | EARTHING CONDUCTOR 50 X 6 mm for Raiser GI Earth Flat) | LOT |  | 1
18.3 | EARTHING DEVICE INCLUDING ITS ASSOCI-ATED ACCESSORIES(50 mm heavy duty GI PIPE 3.0 mtrs long for treated earth pit) | LOT |  | 1
18.4 | EARTHING ROD: 40mm MS rod 3 mtrs long for non treated earth pit. | LOT |  | 1
18.5 | BAY MARSHALLING KIOSK (For S/S: 01 Nos 132 kv bay & 01 Nos 33 kv Bay | NOS |  | 2
18.6 | SWITCH YARD AC CONSOLE FOR LIGHTING ( 01 Nos 132 kv bay & 01 Nos 33 kv Bay ) | NOS |  | 2
18.7 | SWITCH YARD RECEPTACLE BOARD FOR TFR OIL FILTERATION (01 no. near 132/33 KV Tfr) | NOS |  | 1
18.8 | 132KV CT & 33 KV CT & PT CONSOLE BOX | NOS |  | 11
18.9 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY ( 01 Nos 132 kv bay & 01 Nos 33 kv Bay ) | NOS |  | 1
19 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 132/33 KV CLASS
20 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
20.1 | T1S - 132 KV(NOMINAL UNIT WT- 1.2 MT) | NOS | 1.2 | 5
20.2 | T4S - 132KV (NOMINAL UNIT WT- 0.95 MT) | NOS | 0.95 | 4
21 | DIFFERENT TYPE OF BEAMS WITH DETAILS
21.1 | G1 - 132 KV(NOMINAL UNIT WT- 0.62 MT) | NOS | 0.62 | 3
21.2 | G2 - 132 KV(NOMINAL UNIT WT- 0.91 MT) | NOS | 0.91 | 2
21.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT |  | 15
22 | SUPPORT STRUCTURES (LATTICE/PIPE TYPE) FOR ALL 132 KV & 33KV EQUIPMENTS
22.1 | ISOLATORS-132KV
22.1.1 | D.I with E/S | SET | 0.5 | 1
22.1.2 | S.I W/O E/S | SET | 0.38 | 6
22.2 | CT-132 KV | SET | 0.226 | 9
22.3 | CT-33 KV | SET | 0.181 | 15
22.4 | CVT-132 KV | SET | 0.246 | 3
22.5 | IVT-33 KV | SET | 0.134 | 3
22.6 | Surge Arrester-132 kV | SET | 0.226 | 9
22.7 | Wave Trap-132 KV | SET | 0.246 | 2
22.8 | BPI-132 KV | SET | 0.226 | 5
22.9 | BPI-33 KV | SET | 0.134 | 6
22.10 | NCTS (36 KV Class) | SET | 0.226 | 4
22.11 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT |  | 15
22.12 | TOTAL WEIGHT OF COLUMN & BEAM AND SUPPORT STRUCTURE FOR ABOVE EQUIPMENT( Sl No. 21+22+23) | MT |  | 30
22.13 | Total weight of GI Nuts and bolts for the above structures | MT |  | 3
22.14 | ANY OTHER STRUCTURES IF REQUIRED WITH DETAILS | LOT |  | 1
23 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
23.1 | POWER CABLES,1.1KV,XLPE,ARMOURED, ALUMINIUM CONDUCTOR (As per Specification)
23.1.1 | 3.5 CX185 mm2 | LOT |  | 1
23.1.2 | 3.5 CX120 mm2 | LOT |  | 1
23.1.3 | 3.5 CX70 mm2 | LOT |  | 1
23.1.4 | 3.5 CX35 mm2 | LOT |  | 1
23.1.5 | 4 CX 16 mm2 | LOT |  | 1
23.1.6 | 4 CX 6 mm2 | LOT |  | 1
23.1.7 | 2CX 6 mm2 | LOT |  | 1
23.2 | CONTROL CABLES,1.1 KV, PVC,STRANDED COPPER(As per specification)
23.2.1 | 4 CX 2.5 mm2 | LOT |  | 1
23.2.2 | 5 CX 2.5 mm2 | LOT |  | 1
23.2.3 | 7CX 2.5 mm2 | LOT |  | 1
23.2.4 | 10 CX 2.5 mm2 | LOT |  | 1
23.2.5 | 12 CX 2.5 mm2 | LOT |  | 1
23.2.6 | 16 CX 2.5 mm2 | LOT |  | 1
23.2.7 | 19 CX 2.5 mm2 | LOT |  | 1
23.2.8 | 1CX 100 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | LOT |  | 1
23.3 | Perforated G.I. Cable trays of different size for laying of Power & control cables in cable trenches ,section 1-1 , section 2-2, section3-3, section 4-4 | LOT |  | 1
24 | ACCESSORIES FOR PLCC SYSTEM AS PER TECHNICAL SPECIFICATION
24.1 | 132 kV Line Trap for Pedestal mounting with complete accessories :800A, 0.5 mH, (90-500kHZ),Isc=31.5kA compatible to IEC 353 specifications | NOS |  | 2
24.2 | LINE MATCHING UNIT & LINE MATCHING DISTRIBUTION UNIT | SET |  | 1
24.3 | 12.5 mm OD armoured Co-axial Cable; Impedance: 75 ohms, Insulation Resistance: 100 Meg Ohms Dielectric strength: 5 kV, Signal attenuation: 6 dB/KM (Max) at 500 kHz | MTRS |  | 200
24.4 | EPAX standard complied to ITU-T, G-711,G-712,Q507,Q-517 capacity 16lines/Trunks, specification transducers and interfacing cards for Analog input and Digital output (Optional) | NO |  | 1
24.5 | 25 PAIR ARMOURED JELLY FILLED CABLE | MTRS |  | 500
24.6 | 10 PAIR ARMOURED TELEPHONE CABLES | MTRS |  | 250
24.7 | 4 PAIR NON ARMOURED TELEPHONE CABLES | MTRS |  | 100
24.8 | 4 WIRE TELEPHONE SET | NO |  | 4
24.9 | 2 WIRE TELEPHONE SET | NO |  | 16
24.10 | FAX MACHINE | NO |  | 1
24.11 | PLANTE TYPE BATTERY350 AH(FOR 48 V) | SET |  | 1
24.12 | BATTERY CHARGER FOR 48 V, 75 A Float cum Boost | SET |  | 1
24.13 | 48 V DCDB | SET |  | 1
25 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS)(LED Type lamps & fixtures shall be used for all purpose of Lighting).The quantity of such fixtures are to be evaluated after designing as per the required LUX level indicated in TS-Vol-II. Design for different locations , where illumination to be provided is to be furnished to the owner for approval.
25.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES AND LAMPS(LED) | LOT |  | 1
26 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-Vol-IIA-SCPE OF WORK AT-SL NO 15-ANNEXURE – I-Portable Fire Extinguisher)
'26.1 | FOAM TYPE-9 LTRS | NOS |  | 1
'26.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS |  | 2
'26.3 | DRY POWDER TYPE - 5 KGS | NOS |  | 2
'26.4 | CO2 - 4.5 KGS | NOS |  | 5
'26.5 | CO2 - 9 KGS | NOS |  | 2
'26.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS |  | 1
'26.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND | SET |  | 2
27 | PROTECTION,CONTROL METERING, EVENT LOGGER,BUS BAR PROTN PAN,COMM PAN, RELAY TOOL KITS AS PER TECH SPEC
27.1 | 132 KV SIDE
'27.1.1 | TRANSFORMER PROTN RELAY: 02 NOS DIFFERENTIAL NUMERICAL RELAY,IEC 61850 Protocol Compliant FOR 132 KV SIDE OF 132/33 KV POWER TRANSFORMERS | NOS |  | 2
28 | BATTERY (350 AH PLANTE TYPE) FOR 220 V DC | SET |  | 1
29 | BATTERY CHARGER FOR 220 V, 350 AH BATTERY (FLOAT AND FLOAT CUM BOOST) | SET |  | 1
30 | DISTLED WATER PLANT OF 10 LTR/HR FOR BATTERY BANKS | SET |  | 1
31 | WALKIE TALKIE SET | SET /PAIR |  | 2
32 | PORTABLE ALUMINIUM LADDER EXTENDABLE TYPE OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT INSIDE SWITCH YARD.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 19) | NOS |  | 1
33 | MAINTENANCE TESTING EQUIPMENT (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16 ANNEXURE - II ,INDICATED IN -SCHEDULE OF REQUIREMENTS OF MAINTENANCE EQUIPMENT) | LOT |  | 1
34 | OTHER TOOLS AND PLANTS (T&P's) REQUIREMENT (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 17 ANNEXURE - III ,INDICATED IN SCHEDULE OF REQUIREMENTS OTHER T&P's) | LOT |  | 1
35 | OFFICE FURNITURE (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 18 ANNEXURE - IV ,INDICATED IN SCHEDULE OF REQUIREMENTS OFFICE FURNITURE) & PLACING IN CONTROL ROOM,CONFERENCE ROOM,OFFICE ROOMS,LIBRARY,TESTING LAB,etc. | LOT |  | 1
36 | BEST QUALITY &APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC. | LOT |  | 1
TOTAL OF SUBSTATION (PART-I)-2A
NOTE
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested not to leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value). No rate shall be furnished/obtained after bid opening (Ref clause no 33.4.1 of INB vol-I)
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | In mode of transaction column please indicate Direct/Bought-Out. For Taxes & Duties on Direct/Bought-out items ref clause 6.0 of SCC (Vol-IA)
(Signature) ……………………………………………
( Name) ………………………………………………
| Date : | [5 empty] | ( Designation ) ……………………………………….
| Place : | [5 empty] | (Common Seal) ……………………………………

## Schedule 2B SS_Ganjam
ORISSA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2X12.5MVA 132/33KV Sub-Stations Renovation work at GANJAM with associated works.
Bid Document No. : Sr. G.M-CPC-TENDER-PACKAGE- 66-01 /2011
(Equipment/Materials F&I Price Break-up of Ex-works Prices against PACKAGE GANJAM )
Bidder's Name & Address: |  | To,
Orissa Power Transmission Corporation Ltd.,Bhubneshwar
| PART-I, SCHEDULE-2B (FOR SUBSTATION) |  |  |  | PRICE IN INDIAN RUPEES
SL NO | F&I FOR SUPPLY OF FOLLOWING EQUIPMENTS (As per Technical Specification) | Unit |  | Quantity for 2X12.5 MVA 132/33kV Substation Renovation works at Ganjam.(132 KV Feeder Bay:01 No.,132 KV Transformer Bay:02 Nos,33 KV Transformer Bay: 02 Nos, 33 KV Feeder Bay:03 Nos, 33 KV Bus Coupler Bay:01 No.). | Unit F&I Price | Total F&I Price
1 | 2 | 3 | 0 | 4 | 5 | 6=4X5
1 | 145 KV,800-400-200/1-1-1-1 A,40 KA,4CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 9
2 | 145 KV,1200A,40 KA,ISOLATORS
2.1 | S/I WITH OUT EARTH SWITCH | NOS |  | 6
2.2 | D/I WITH SINGLE EARTH SWITCH | NOS |  | 1
3 | 145 KV,6600pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS |  | 3
4 | 120 KV METAL OXIDE SURGE ARRESTOR, 10 KA, Class III | NOS |  | 9
6 | 132 KV Bus Post Insulators | NOS |  | 5
7 | 145KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 3
8 | 36 KV,(800-400-200/1-1-1 A),25KA,3CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 15
9 | 36 KV Class NCT FOR TRANSFORMER PROTECTION RATING (800-400-200/1-1 A)( IN EACH POWER TRANSFORMER 132 KV SIDE-1 NO) | NOS |  | 2
10 | 36 KV Class NCT FOR TRANSFORMER PROTECTION RATING (800-400-200/1-1 A)( IN EACH POWER TRANSFORMER 33 KV SIDE 1 No.) | NOS |  | 2
11 | 30 KV, METAL OXIDE SURGE ARRESTOR, 10KA, class II | NOS |  | 6
12 | 36 KV ,2 CORE,SINGLE PHASE,IVT | NOS |  | 3
13 | 36KV,1250A,25KA,VACUUM CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 2
14 | 33 KV Bus Post Insulators | NOS |  | 6
15 | BUS BAR & CIRCUIT MATERIALS( all insulators as indicated below shall be of “LONG ROD ” Type
15.1 | 120 KN INSULATOR STRINGS(TENSION for single ACSR Moose)-132 KV | SET |  | 18
15.2 | 120 KN INSULATOR STRINGS(TENSION for Single ACSR Moose)-33 KV | SET |  | 9
15.3 | 120 KN INSULATOR STRINGS (SUSPENSION for single ACSR Moose)-132 KV | SET |  | 12
15.4 | 120 KN INSULATOR STRINGS (SUSPENSION for Single ACSR Moose)-33 KV | SET |  | 9
16 | ACSR MOOSE CONDUCTOR | KM |  | 0.5
17 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | LOT |  | 1
18 | SUBSTATION SYSTEMS
18.1 | EARTHING CONDUCTOR (75x10mm for laying (spacing maximum 5m) (GI FLAT) | LOT |  | 1
18.2 | EARTHING CONDUCTOR 50 X 6 mm for Raiser GI Earth Flat) | LOT |  | 1
18.3 | EARTHING DEVICE INCLUDING ITS ASSOCI-ATED ACCESSORIES(50 mm heavy duty GI PIPE 3.0 mtrs long for treated earth pit) | LOT |  | 1
18.4 | EARTHING ROD: 40mm MS rod 3 mtrs long for non treated earth pit. | LOT |  | 1
18.5 | BAY MARSHALLING KIOSK (For S/S: 01 Nos 132 kv bay & 01 Nos 33 kv Bay | NOS |  | 2
18.6 | SWITCH YARD AC CONSOLE FOR LIGHTING ( 01 Nos 132 kv bay & 01 Nos 33 kv Bay ) | NOS |  | 2
18.7 | SWITCH YARD RECEPTACLE BOARD FOR TFR OIL FILTERATION (01 no. near 132/33 KV Tfr) | NOS |  | 1
18.8 | 132KV CT & 33 KV CT & PT CONSOLE BOX | NOS |  | 11
18.9 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY ( 01 Nos 132 kv bay & 01 Nos 33 kv Bay ) | NOS |  | 1
19 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 132/33 KV CLASS
20 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
20.1 | T1S - 132 KV(NOMINAL UNIT WT- 1.2 MT) | NOS | 1.2 | 5
20.2 | T4S - 132KV (NOMINAL UNIT WT- 0.95 MT) | NOS | 0.95 | 4
21 | DIFFERENT TYPE OF BEAMS WITH DETAILS
21.1 | G1 - 132 KV(NOMINAL UNIT WT- 0.62 MT) | NOS | 0.62 | 3
21.2 | G2 - 132 KV(NOMINAL UNIT WT- 0.91 MT) | NOS | 0.91 | 2
21.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT |  | 15
22 | SUPPORT STRUCTURES (LATTICE/PIPE TYPE) FOR ALL 132 KV & 33KV EQUIPMENTS
22.1 | ISOLATORS-132KV
22.1.1 | D.I with E/S | SET | 0.5 | 1
22.1.2 | S.I W/O E/S | SET | 0.38 | 6
22.2 | CT-132 KV | SET | 0.226 | 9
22.3 | CT-33 KV | SET | 0.181 | 15
22.4 | CVT-132 KV | SET | 0.246 | 3
22.5 | IVT-33 KV | SET | 0.134 | 3
22.6 | Surge Arrester-132 kV | SET | 0.226 | 9
22.7 | Wave Trap-132 KV | SET | 0.246 | 2
22.8 | BPI-132 KV | SET | 0.226 | 5
22.9 | BPI-33 KV | SET | 0.134 | 6
22.10 | NCTS (36 KV Class) | SET | 0.226 | 4
22.11 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT |  | 15
22.12 | TOTAL WEIGHT OF COLUMN & BEAM AND SUPPORT STRUCTURE FOR ABOVE EQUIPMENT( Sl No. 21+22+23) | MT |  | 30
22.13 | Total weight of GI Nuts and bolts for the above structures | MT |  | 3
22.14 | ANY OTHER STRUCTURES IF REQUIRED WITH DETAILS | LOT |  | 1
23 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
23.1 | POWER CABLES,1.1KV,XLPE,ARMOURED, ALUMINIUM CONDUCTOR (As per Specification)
23.1.1 | 3.5 CX185 mm2 | LOT |  | 1
23.1.2 | 3.5 CX120 mm2 | LOT |  | 1
23.1.3 | 3.5 CX70 mm2 | LOT |  | 1
23.1.4 | 3.5 CX35 mm2 | LOT |  | 1
23.1.5 | 4 CX 16 mm2 | LOT |  | 1
23.1.6 | 4 CX 6 mm2 | LOT |  | 1
23.1.7 | 2CX 6 mm2 | LOT |  | 1
23.2 | CONTROL CABLES,1.1 KV, PVC,STRANDED COPPER(As per specification)
23.2.1 | 4 CX 2.5 mm2 | LOT |  | 1
23.2.2 | 5 CX 2.5 mm2 | LOT |  | 1
23.2.3 | 7CX 2.5 mm2 | LOT |  | 1
23.2.4 | 10 CX 2.5 mm2 | LOT |  | 1
23.2.5 | 12 CX 2.5 mm2 | LOT |  | 1
23.2.6 | 16 CX 2.5 mm2 | LOT |  | 1
23.2.7 | 19 CX 2.5 mm2 | LOT |  | 1
23.2.8 | 1CX 100 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | LOT |  | 1
23.3 | Perforated G.I. Cable trays of different size for laying of Power & control cables in cable trenches ,section 1-1 , section 2-2, section3-3, section 4-4 | LOT |  | 1
24 | ACCESSORIES FOR PLCC SYSTEM AS PER TECHNICAL SPECIFICATION
24.1 | 132 kV Line Trap for Pedestal mounting with complete accessories :800A, 0.5 mH, (90-500kHZ),Isc=31.5kA compatible to IEC 353 specifications | NOS |  | 2
24.2 | LINE MATCHING UNIT & LINE MATCHING DISTRIBUTION UNIT | SET |  | 1
24.3 | 12.5 mm OD armoured Co-axial Cable; Impedance: 75 ohms, Insulation Resistance: 100 Meg Ohms Dielectric strength: 5 kV, Signal attenuation: 6 dB/KM (Max) at 500 kHz | MTRS |  | 200
24.4 | EPAX standard complied to ITU-T, G-711,G-712,Q507,Q-517 capacity 16lines/Trunks, specification transducers and interfacing cards for Analog input and Digital output (Optional) | NO |  | 1
24.5 | 25 PAIR ARMOURED JELLY FILLED CABLE | MTRS |  | 500
24.6 | 10 PAIR ARMOURED TELEPHONE CABLES | MTRS |  | 250
24.7 | 4 PAIR NON ARMOURED TELEPHONE CABLES | MTRS |  | 100
24.8 | 4 WIRE TELEPHONE SET | NO |  | 4
24.9 | 2 WIRE TELEPHONE SET | NO |  | 16
24.10 | FAX MACHINE | NO |  | 1
24.11 | PLANTE TYPE BATTERY350 AH(FOR 48 V) | SET |  | 1
24.12 | BATTERY CHARGER FOR 48 V, 75 A Float cum Boost | SET |  | 1
24.13 | 48 V DCDB | SET |  | 1
25 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS)(LED Type lamps & fixtures shall be used for all purpose of Lighting).The quantity of such fixtures are to be evaluated after designing as per the required LUX level indicated in TS-Vol-II. Design for different locations , where illumination to be provided is to be furnished to the owner for approval.
25.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES AND LAMPS(LED) | LOT |  | 1
26 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-Vol-IIA-SCPE OF WORK AT-SL NO 15-ANNEXURE – I-Portable Fire Extinguisher)
'26.1 | FOAM TYPE-9 LTRS | NOS |  | 1
'26.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS |  | 2
'26.3 | DRY POWDER TYPE - 5 KGS | NOS |  | 2
'26.4 | CO2 - 4.5 KGS | NOS |  | 5
'26.5 | CO2 - 9 KGS | NOS |  | 2
'26.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS |  | 1
'26.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND | SET |  | 2
27 | PROTECTION,CONTROL METERING, EVENT LOGGER,BUS BAR PROTN PAN,COMM PAN, RELAY TOOL KITS AS PER TECH SPEC
27.1 | 132 KV SIDE
'27.1.1 | TRANSFORMER PROTN RELAY: 02 NOS DIFFERENTIAL NUMERICAL RELAY,IEC 61850 Protocol Compliant FOR 132 KV SIDE OF 132/33 KV POWER TRANSFORMERS | NOS |  | 2
28 | BATTERY (350 AH PLANTE TYPE) FOR 220 V DC | SET |  | 1
29 | BATTERY CHARGER FOR 220 V, 350 AH BATTERY (FLOAT AND FLOAT CUM BOOST) | SET |  | 1
30 | DISTLED WATER PLANT OF 10 LTR/HR FOR BATTERY BANKS | SET |  | 1
31 | WALKIE TALKIE SET | SET /PAIR |  | 2
32 | PORTABLE ALUMINIUM LADDER EXTENDABLE TYPE OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT INSIDE SWITCH YARD.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 19) | NOS |  | 1
33 | MAINTENANCE TESTING EQUIPMENT (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16 ANNEXURE - II ,INDICATED IN -SCHEDULE OF REQUIREMENTS OF MAINTENANCE EQUIPMENT) | LOT |  | 1
34 | OTHER TOOLS AND PLANTS (T&P's) REQUIREMENT (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 17 ANNEXURE - III ,INDICATED IN SCHEDULE OF REQUIREMENTS OTHER T&P's) | LOT |  | 1
35 | OFFICE FURNITURE (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 18 ANNEXURE - IV ,INDICATED IN SCHEDULE OF REQUIREMENTS OFFICE FURNITURE) & PLACING IN CONTROL ROOM,CONFERENCE ROOM,OFFICE ROOMS,LIBRARY,TESTING LAB,etc. | LOT |  | 1
36 | BEST QUALITY &APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC. | LOT |  | 1
TOTAL OF SUBSTATION (PART-I)-2B
NOTE
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested not to leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value). No rate shall be furnished/obtained after bid opening (Ref clause no 33.4.1 of INB vol-I)
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | Bidder should be quoted including service tax, no service tax shall be paid/reimbursed.
| Date : | (Signature) ……………………………………………
| Place : | ( Name) ………………………………………………
( Designation ) ……………………………………….
(Common Seal) ……………………………………

## Schedule 2C SS _Ganjam_
ORISSA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2X12.5MVA 132/33KV Sub-Stations Renovation work at GANJAM with associated works.
Bid Document No. : Sr. G.M-CPC-TENDER-PACKAGE- 66-01 /2011
(Equipment/Materials Price Break-up of ERECTION Prices against PACKAGE GANJAM )
Bidder's Name & Address: |  | To,
Orissa Power Transmission Corporation Ltd.,Bhubneshwar
| PART-I, SCHEDULE-2C (FOR SUBSTATION) |  |  |  | Erection charges (PRICE IN INDIAN RUPEES)
SL NO | DESCRIPTION OF ITEMS | Unit |  | Quantity for 2X12.5 MVA 132/33kV Substation Renovation works at Ganjam.(132 KV Feeder Bay:01 No.,132 KV Transformer Bay:02 Nos,33 KV Transformer Bay: 02 Nos, 33 KV Feeder Bay:03 Nos, 33 KV Bus Coupler Bay:01 No.). | Unit Rate | Total Price
ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification)
1 | 2 | 3 |  | 4 | 5 | 6=4X5
A | ELECTRICAL WORKS
1 | 145 KV,800-400-200/1-1-1-1 A,40 KA,4CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 9
2 | 145 KV,1200A,40 KA,ISOLATORS
2.1 | S/I WITH OUT EARTH SWITCH | NOS |  | 6
2.2 | D/I WITH SINGLE EARTH SWITCH | NOS |  | 1
3 | 145 KV,6600pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS |  | 3
4 | 120 KV METAL OXIDE SURGE ARRESTOR, 10 KA, Class III | NOS |  | 9
6 | 132 KV Bus Post Insulators | NOS |  | 5
7 | 145KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 3
8 | 36 KV,(800-400-200/1-1-1 A),25KA,3CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 15
9 | 36 KV Class NCT FOR TRANSFORMER PROTECTION RATING (800-400-200/1-1 A)( IN EACH POWER TRANSFORMER 132 KV SIDE-1 NO) | NOS |  | 2
10 | 36 KV Class NCT FOR TRANSFORMER PROTECTION RATING (800-400-200/1-1 A)( IN EACH POWER TRANSFORMER 33 KV SIDE 1 No.) | NOS |  | 2
11 | 30 KV, METAL OXIDE SURGE ARRESTOR, 10KA, class II | NOS |  | 6
12 | 36 KV ,2 CORE,SINGLE PHASE,IVT | NOS |  | 3
13 | 36KV,1250A,25KA,VACUUM CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 2
14 | 33 KV Bus Post Insulators | NOS |  | 6
15 | BUS BAR & CIRCUIT MATERIALS( all insulators as indicated below shall be of “LONG ROD ” Type
15.1 | 120 KN INSULATOR STRINGS(TENSION for single ACSR Moose)-132 KV | SET |  | 18
15.2 | 120 KN INSULATOR STRINGS(TENSION for Single ACSR Moose)-33 KV | SET |  | 9
15.3 | 120 KN INSULATOR STRINGS (SUSPENSION for single ACSR Moose)-132 KV | SET |  | 12
15.4 | 120 KN INSULATOR STRINGS (SUSPENSION for Single ACSR Moose)-33 KV | SET |  | 9
16 | ACSR MOOSE CONDUCTOR | KM |  | 0.5
17 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | LOT |  | 1
18 | SUBSTATION SYSTEMS
18.1 | EARTHING CONDUCTOR (75x10mm for laying (spacing maximum 5m) (GI FLAT) | LOT |  | 1
18.2 | EARTHING CONDUCTOR 50 X 6 mm for Raiser GI Earth Flat) | LOT |  | 1
18.3 | EARTHING DEVICE INCLUDING ITS ASSOCI-ATED ACCESSORIES(50 mm heavy duty GI PIPE 3.0 mtrs long for treated earth pit) | LOT |  | 1
18.4 | EARTHING ROD: 40mm MS rod 3 mtrs long for non treated earth pit. | LOT |  | 1
18.5 | BAY MARSHALLING KIOSK (For S/S: 01 Nos 132 kv bay & 01 Nos 33 kv Bay | NOS |  | 2
18.6 | SWITCH YARD AC CONSOLE FOR LIGHTING ( 01 Nos 132 kv bay & 01 Nos 33 kv Bay ) | NOS |  | 2
18.7 | SWITCH YARD RECEPTACLE BOARD FOR TFR OIL FILTERATION (01 no. near 132/33 KV Tfr) | NOS |  | 1
18.8 | 132KV CT & 33 KV CT & PT CONSOLE BOX | NOS |  | 11
18.9 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY ( 01 Nos 132 kv bay & 01 Nos 33 kv Bay ) | NOS |  | 1
19 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 132/33 KV CLASS
20 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
20.1 | T1S - 132 KV(NOMINAL UNIT WT- 1.2 MT) | NOS | 1.2 | 5
20.2 | T4S - 132KV (NOMINAL UNIT WT- 0.95 MT) | NOS | 0.95 | 4
21 | DIFFERENT TYPE OF BEAMS WITH DETAILS
21.1 | G1 - 132 KV(NOMINAL UNIT WT- 0.62 MT) | NOS | 0.62 | 3
21.2 | G2 - 132 KV(NOMINAL UNIT WT- 0.91 MT) | NOS | 0.91 | 2
21.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT |  | 15
22 | SUPPORT STRUCTURES (LATTICE/PIPE TYPE) FOR ALL 132 KV & 33KV EQUIPMENTS
22.1 | ISOLATORS-132KV
22.1.1 | D.I with E/S | SET | 0.5 | 1
22.1.2 | S.I W/O E/S | SET | 0.38 | 6
22.2 | CT-132 KV | SET | 0.226 | 9
22.3 | CT-33 KV | SET | 0.181 | 15
22.4 | CVT-132 KV | SET | 0.246 | 3
22.5 | IVT-33 KV | SET | 0.134 | 3
22.6 | Surge Arrester-132 kV | SET | 0.226 | 9
22.7 | Wave Trap-132 KV | SET | 0.246 | 2
22.8 | BPI-132 KV | SET | 0.226 | 5
22.9 | BPI-33 KV | SET | 0.134 | 6
22.10 | NCTS (36 KV Class) | SET | 0.226 | 4
22.11 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT |  | 15
22.12 | TOTAL WEIGHT OF COLUMN & BEAM AND SUPPORT STRUCTURE FOR ABOVE EQUIPMENT( Sl No. 21+22+23) | MT |  | 30
22.13 | Total weight of GI Nuts and bolts for the above structures | MT |  | 3
22.14 | ANY OTHER STRUCTURES IF REQUIRED WITH DETAILS | LOT |  | 1
23 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
23.1 | POWER CABLES,1.1KV,XLPE,ARMOURED, ALUMINIUM CONDUCTOR (As per Specification)
23.1.1 | 3.5 CX185 mm2 | LOT |  | 1
23.1.2 | 3.5 CX120 mm2 | LOT |  | 1
23.1.3 | 3.5 CX70 mm2 | LOT |  | 1
23.1.4 | 3.5 CX35 mm2 | LOT |  | 1
23.1.5 | 4 CX 16 mm2 | LOT |  | 1
23.1.6 | 4 CX 6 mm2 | LOT |  | 1
23.1.7 | 2CX 6 mm2 | LOT |  | 1
23.2 | CONTROL CABLES,1.1 KV, PVC,STRANDED COPPER(As per specification)
23.2.1 | 4 CX 2.5 mm2 | LOT |  | 1
23.2.2 | 5 CX 2.5 mm2 | LOT |  | 1
23.2.3 | 7CX 2.5 mm2 | LOT |  | 1
23.2.4 | 10 CX 2.5 mm2 | LOT |  | 1
23.2.5 | 12 CX 2.5 mm2 | LOT |  | 1
23.2.6 | 16 CX 2.5 mm2 | LOT |  | 1
23.2.7 | 19 CX 2.5 mm2 | LOT |  | 1
23.2.8 | 1CX 100 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | LOT |  | 1
23.3 | Perforated G.I. Cable trays of different size for laying of Power & control cables in cable trenches ,section 1-1 , section 2-2, section3-3, section 4-4 | LOT |  | 1
24 | ACCESSORIES FOR PLCC SYSTEM AS PER TECHNICAL SPECIFICATION
24.1 | 132 kV Line Trap for Pedestal mounting with complete accessories :800A, 0.5 mH, (90-500kHZ),Isc=31.5kA compatible to IEC 353 specifications | NOS |  | 2
24.2 | LINE MATCHING UNIT & LINE MATCHING DISTRIBUTION UNIT | SET |  | 1
24.3 | 12.5 mm OD armoured Co-axial Cable; Impedance: 75 ohms, Insulation Resistance: 100 Meg Ohms Dielectric strength: 5 kV, Signal attenuation: 6 dB/KM (Max) at 500 kHz | MTRS |  | 200
24.4 | EPAX standard complied to ITU-T, G-711,G-712,Q507,Q-517 capacity 16lines/Trunks, specification transducers and interfacing cards for Analog input and Digital output (Optional) | NO |  | 1
24.5 | 25 PAIR ARMOURED JELLY FILLED CABLE | MTRS |  | 500
24.6 | 10 PAIR ARMOURED TELEPHONE CABLES | MTRS |  | 250
24.7 | 4 PAIR NON ARMOURED TELEPHONE CABLES | MTRS |  | 100
24.8 | 4 WIRE TELEPHONE SET | NO |  | 4
24.9 | 2 WIRE TELEPHONE SET | NO |  | 16
24.10 | FAX MACHINE | NO |  | 1
24.11 | PLANTE TYPE BATTERY350 AH(FOR 48 V) | SET |  | 1
24.12 | BATTERY CHARGER FOR 48 V, 75 A Float cum Boost | SET |  | 1
24.13 | 48 V DCDB | SET |  | 1
25 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS)(LED Type lamps & fixtures shall be used for all purpose of Lighting).The quantity of such fixtures are to be evaluated after designing as per the required LUX level indicated in TS-Vol-II. Design for different locations , where illumination to be provided is to be furnished to the owner for approval.
25.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES AND LAMPS(LED) | LOT |  | 1
26 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-Vol-IIA-SCPE OF WORK AT-SL NO 15-ANNEXURE – I-Portable Fire Extinguisher)
'26.1 | FOAM TYPE-9 LTRS | NOS |  | 1
'26.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS |  | 2
'26.3 | DRY POWDER TYPE - 5 KGS | NOS |  | 2
'26.4 | CO2 - 4.5 KGS | NOS |  | 5
'26.5 | CO2 - 9 KGS | NOS |  | 2
'26.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS |  | 1
'26.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND | SET |  | 2
27 | PROTECTION,CONTROL METERING, EVENT LOGGER,BUS BAR PROTN PAN,COMM PAN, RELAY TOOL KITS AS PER TECH SPEC
27.1 | 132 KV SIDE
'27.1.1 | TRANSFORMER PROTN RELAY: 02 NOS DIFFERENTIAL NUMERICAL RELAY,IEC 61850 Protocol Compliant FOR 132 KV SIDE OF 132/33 KV POWER TRANSFORMERS | NOS |  | 2
28 | BATTERY (350 AH PLANTE TYPE) FOR 220 V DC | SET |  | 1
29 | BATTERY CHARGER FOR 220 V, 350 AH BATTERY (FLOAT AND FLOAT CUM BOOST) | SET |  | 1
30 | DISTLED WATER PLANT OF 10 LTR/HR FOR BATTERY BANKS | SET |  | 1
31 | WALKIE TALKIE SET | SET /PAIR |  | 2
32 | PORTABLE ALUMINIUM LADDER EXTENDABLE TYPE OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT INSIDE SWITCH YARD.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 19) | NOS |  | 1
33 | BEST QUALITY &APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC. | LOT |  | 1
34 | ERECTION OF PLCC EQUIPMENT SUPPLIED BY OWNER INCLUDING DISMANTLING FROM EXISTING SUBSTATION ( AS PER THE DETAILS SLD GIVEN IN TS) AND TRANSPORTATION AS REQUIRED | LOT |  | 1
TOTAL of Part-I (A)
B | CIVIL WORKS
1 | Foundations : Design, engineering, supply of all labour, material (Cement-OPC-43 Grade,MS Rod, coarse and fine aggregates(Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation,concreting, shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal structures and equipment support & others as per the technical specification and approved drawings.(RCC RATIO 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge.
1.1 | Excavation:This also Includes excavation in all types of soil or rocks,back filling and disposal of excess earth as per the direction of Engineer In Charge | CUM |  | 4000
1.2 | Open cast foundation for the above column/equipment/marshalling box foundations { Sl No. 1.6 & 1.7} with RCC: 1:1.5:3 (Grade M-20),including supply of Labour all materials like Steel (Supply,Cutting,Bending,Binding (including supply of binding wire) and placing in position of steel rods of different size as per design in the foundation pit as required for the above foundations),Cement, coarse and fine aggregates,shuttering,proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. | CUM |  | 900
1.3 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM |  | 80
1.4 | Brick Masonary work in cement and sand mortar 1:6 with bricks of class designation 75 as per technical specification and as directed by Engineer In Charge. | CUM |  | 100
1.5 | 12 mm thick plaster in cement sand mortar ( 1: 6 ) as per technical specification and as directed by Engineer In Charge. | Sq.Mtr |  | 800
1.6 | Switchyard gantry/portal structure foundations.
'1.6.1 | T1S | Nos |  | 5
'1.6.2 | T4S | Nos |  | 4
1.7 | Switch yard Equipment /Marshaling Boxes foundations
'1.7.1 | 145kV circuit breaker | Nos |  | 3
'1.7.2 | (a) 145 KV Isolators (S/I) | Nos |  | 6
'1.7.3 | (b) 145kV isolators (D/I)( W E/S) | Nos |  | 1
'1.7.4 | 145kV current transformers | Nos |  | 9
'1.7.5 | 120kV surge arrestors | Nos |  | 9
'1.7.6 | 145kV bus post Insulators | Nos |  | 5
'1.7.7 | 145 KV Line /Wave Trap | NOS |  | 2
'1.7.8 | 36kV voltage transformers | Nos |  | 3
'1.7.9 | 36kV bus post insulators | Nos |  | 6
'1.7.10 | Marshaling boxes ( Bay Marshaling boxes etc) | Nos |  | 2
'1.7.11 | Junction boxes (Receptacle panels for welding and other emergency works etc) | Nos |  | 1
'1.7.12 | Junction boxes (AC console box near Transformer for oil filtration work) | Nos |  | 1
'1.7.13 | Junction boxes (switch yard lighting panels) | Nos |  | 2
'1.7.14 | NCT for Power Transformer | Nos |  | 4
2 | Cable Trenches: Design, engineering, and construction of RCC(1:1.5:3) cable trenches and all associated works for cable trench crossings to the required depths, precast RCC covers(1:1.5:3), water stops, brickwork with plastering wherever required including the supply of labour,material, cement, reinforcement steel, form work, steel angles(G.I), flats(G.I) and providing PCC(1:3:6) below cable trenches as per technical specifications and approved drawings and as per direction of the Project Manager. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. *CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE INCLUDING STANDARD SUPPORT.
2.1 | Cable trench with covers
2.1.1 | Section 1-1 | Mtrs |  | 100
2.1.2 | Section 2- 2 | Mtrs |  | 50
2.1.3 | Section 3-3 | Mtrs |  | 50
2.1.4 | Section 4-4 | Mtrs |  | 100
2.2 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,form work etc,and all associated works for construction of trench crossing as per technical specification and approved drawing.
2.2.1 | Road crossing for
2.2.1.1 | Section 1-1 | Lot |  | 1
2.2.1.2 | Section 2- 2 | Lot |  | 1
2.2.1.3 | Section 3-3 | Lot |  | 1
3 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme, road-culverts, and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. All the switch yard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification.
3.1 | Storm water drain as per technical specification | Lot |  | 1
3.2 | Road-culverts, (including one no for approach raod) drain crossings | Lot |  | 1
3.3 | Cable trench crossing | Lot |  | 1
4 | Substation earth mat Design, engineering, supply{(except the GI Flats,GI Pipe,M.S Rod)(only erection)} inclusive of corrosion protection measures if any,laying of earth mat conductors of Hot dip galvanised flats of size 75X10mm to the approval of Project Manager, excavation, welding/jointing of ground conductors along with risers (a) upto Finished level from the mat size 75X10 mm GI flats & b) from the finished ground level to the top of the structure and equipment shall be with 50X6 mm GI Flats, with back filling and good compaction,grounding driven rods(40 mm MS solid rod for untreated earth pit ,perforated 50 mm Mid GI pipes for treated earth pits(with details of treatment as per IS). The spacing between the earth conductor not more than 5 mtrs (both way) and to be buried at depth of 700mm from the finished ground level. For provision of treated earth pit and untreated earth pit, refer the specification for designing. Provision of water taps inside the switch yard areas and peripheral treated and nu-treated earth pit are required to be provided for watering the treated earth pits. The no. of treated and un-treated earth pits are to be done as per the practice and as indicated in the drawing for different equipments. This is as per approved drawing and specification.
4.1 | EARTHING CONDUCTOR (75x10mm for laying (spacing maximum 5m) (GI FLAT)(Excavation of trench as per technical spec and as directed by Engineer in Charge) | LOT |  | 1
4.2 | EARTHING DEVICE INCLUDING ITS ASSOCI-ATED ACCESSORIES(50 mm heavy duty GI PIPE 3.0 mtrs long for treated earth pit) (Excavation and construction of earth pit as per technical spec and as directed by Engineer in Charge) | LOT |  | 1
5 | Leveling the switch yard area before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area .After proper leveling of the switch yard area (after anti-weed treatment), and maintaining proper sloping for easy discharge of storm water . As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. This also includes excavation in all types of soil or rocks,back filling with borrowed earth/good quality river bed sand if required beyond 30 mtrs lead ,and disposal of excess earth as per the direction of Engineer In charge and approved drawing.
5.1 | Contour survey of the entire sub-station area including Supply of all labour & T&P by contractor. | SQM |  | 5000
5.2 | Cutting of sub-station area of the as per the direction of Engineer in Charge. | Cum |  | 250
5.3 | Filling with borrowed earth beyond 30 mtrs lead as per the direction of Engineer in Charge. | Cum |  | 750
6 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area .Proper leveling of the switch yard area, anti-weed treatment, spreading of plain cement concrete with mixing ratio 1:4:8 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area . As per technical specification and approved drawing, and as per the instruction of the Engineer-in-Charge. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. | LOT |  | 1
7 | Metal Spreading:Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the compacted good quality sand.The total compacted thickness of the metals(20 mm Nominal) 100 mm above the sand compaction. | LOT |  | 1
8 | Switch yard fencing: Providing and fixing of G.I Goat mesh (2.5 mm dia) fencing( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, state and central government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Brick masonry work with ratio 1:5 and cement pointing of the joints, for the fencing up to a height from the finished ground level) .This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing as per specification. | LOT |  | 1
9 | Fire wall: Design, engineering, procurement of labour, material including all associated works for construction of fire-walls as per technical specification and approved drawings(column shall be RCC ratio1:1.5:3 and the walls are of fire resistant bricks).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. Painting of the walls as per direction of the Site In charge | Nos |  | 1
10 | Any other civil work to be included in the schedule by the Bidder if required essential for successful completion of project, including supply of labour, material, cement reinforcement steel, form work etc. Bidder shall also quote the unit rate for the following items of works.(Rate shall be inclusive of supply of labour, material, cement, reinforcement steel, form work etc. )
10.1 | Excavation of soil. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. | Cu.m. |  | 1
10.2 | PCC: M10(1: 3 : 6) | Cu.m. |  | 1
10.3 | RCC M 15(1:2:4) | Cu.m. |  | 1
10.4 | RCC: M 20(1:1.5:3) | Cu.m. |  | 1
10.5 | Brick masonry work in cement sand mortar 1: 6 with bricks of class designation 75. | Cu.m. |  | 1
10.6 | 12 mm thick plaster in cement sand mortar ( 1: 6 ). | Sq.m. |  | 1
10.7 | Cutting,bending,binding(supply of binding wires) and fixing of reinforcement(including supply of reinforcement). | M.T. |  | 1
11 | COLOUR CODING, BAY MARKING Etc:Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof snickering may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. MS sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot |  | 1
12 | Dismantling of existing switchyard structure and proper stacking,storing and handing over to OPTCL as per the direction of Engineer In Charge. | MT |  | 20
13 | Dismantling of existing foundation and removal of the debris es and disposal of the same as per the direction of Engineer In Charge | CUM |  | 300
TOTAL OF CIVIL WORKS (B)
GRAND TOTAL ( ELECTRICAL WORKS + CIVIL WORKS) (A+B)-PART-I-2C
NOTE:
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested not to leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value). No rate shall be furnished/obtained after bid opening (Ref clause no 33.4.1 of INB vol-I) .
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | Bidder has to quote rates excluding service tax (if any), service tax shall be paid/reimbursed as per conditions of Bid Document.
| Date : | (Signature) ……………………………………………
| Place : | ( Name) ………………………………………………
( Designation ) ……………………………………….
(Common Seal) ……………………………………