## Schedule 2C SS
ORISSA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2X160 MVA,220/132 Sub-Station along with 132KV Transmission Lines and associated system
At MENDHASAL
Bid Document No. : Sr. G.M-CPC-TENDER-PACKAGE- 61-02 /2012
(Equipment/Materials Price Break-up of Ex-works Prices against PACKAGE 61-02 / 2012 )
PART-I, SCHEDULE-2C (FOR SUBSTATION) |  |  |  |  | PRICE IN INDIAN RUPEES
SL NO | DESCRIPTION OF ITEMS | Unit |  | Quantity for 2X160 MVA,220/132 Substation at MENDHASAL [02 Nos 220 KV TRANSFORMER Bays,7 Nos(2Fdr+2T+1B/C+2 SPARE)132 KV Bays. | Erection charges
| ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) |  |  |  | Unit Rate | Total Price
1 | 2 | 3 |  | 4 | 5 | 6
A | ELECTRICAL WORKS
1 | 245 KV,1200-600-300A,40KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 6
2 | 245 KV,1600A,40KA,ISOLATORS
2.1 | WITH OUT EARTH SWITCH | NOS |  | 2
2.2 | WITH SINGLE EARTH SWITCH | NOS |  | 2
2.3 | TANDEM WITHOUT EARTH SWITCH | NOS |  | 4
3 | 245KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 2
4 | 216 KV, METAL OXIDE SURGE ARRESTOR,10 KA, class III | NOS |  | 6
5 | 220 KV Bus Post Insulators | NOS |  | 14
6 | 145 KV,(Different Ratio),40 KA,4CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 15
7 | 145 KV,1200A,40 KA,ISOLATORS
7.1 | S/I WITH OUT EARTH SWITCH (Includes section switches at the main bus near B/C ) | NOS |  | 8
7.2 | D/I WITH SINGLE EARTH SWITCH | NOS |  | 2
7.3 | D/I WITHOUT EARTH SWITCH | NOS |  | 2
8 | 145 KV, 6000pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS |  | 6
9 | 120 KV METAL OXIDE SURGE ARRESTOR, 10 KA, Class III | NOS |  | 12
10 | 145 KV ,2 CORE,SINGLE PHASE,IVT | NOS |  | 3
11 | 132 KV Bus Post Insulators | NOS |  | 18
12 | 145KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 5
13 | 36 KV CLASS NCT FOR TRANSFORMER PROTECTION RATING AS DECIDED (RATINGS AS PER THE SUITABILITY) HAVING TWO CORE (IN EACH AUTO TRANSFORMER 1 No. NCT ) | NOS |  | 2
14 | BUS BAR & CIRCUIT MATERIALS
14.1 | FOLLOWING ANTI FOG TYPE DISC INSULATORS
14.1.1 | 160 kN INSULATOR STRINGS for twin Moose cond ( TENSION)-220 KV | SET |  | 24
14.1.2 | 160 kN INSULATOR STRINGS for single Moose cond (TENSION)-220 KV | SET |  | 48
14.1.3 | 120 kN INSULATOR STRINGS for Double Moose cond (TENSION)-132 KV | SET |  | 18
14.1.4 | 120 kN INSULATOR STRINGS for Single Moose cond( TENSION)-132 KV | SET |  | 54
14.1.5 | 90 kN INSULATOR STRINGS for Double/ Single Moose cond ( SUSPENSION)-220 KV | SET |  | 36
14.1.6 | 90 kN INSULATOR STRINGS for Double/ Single Moose cond ( SUSPENSION)-132 KV | SET |  | 24
14.2 | ACSR MOOSE CONDUCTOR | LOT |  | 1
14.3 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | LOT |  | 1
14.4 | EARTH WIRES & IT'S HARDWARES & FITTING, with copper earth bond | LOT |  | 1
15 | SUBSTATION SYSTEMS
15.1 | EARTHING CONDUCTOR FOR BURRIAL : 40 mm DIA MS ROD for laying (spacing maximum 5m) (Substation earth mat): Design, engineering, supply (except the MS Rods, only erection) inclusive of corrosion protection measures if any,laying of earth mat conductors of size 40 mm dia MS Rod as per the approval of Engineer in charge, excavation, welding/jointing of ground conductors along with risers (a) up to Finished level from the mat size 40 mm MS rods. with back filling and good compaction,The spacing between the earth conductor not more than 5 mtrs (both way) and to be buried at depth of 700mm from the finished ground level as per the practice and as per specification. | LOT |  | 1
15.2 | EARTHING CONDUCTOR: 75x10mm GI Flat for Raiser from the burial earth mat to equipment,structure including proper welding, bending and anti corrosive painting etc from the finished ground level to the top of the structure and equipment shall be with 75X10 mm GI Flats, as per approved drawing and specification. | LOT |  | 1
15.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit): perforated 50 mm Heavy duty GI pipes for treated earth pits (with details of treatment as per IS) including, excavation,supply of Bentonate powder and other materials for the treated earth pit as per standard practice and as per specification. | LOT |  | 1
15.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) to be inserted directly inside the soil. | LOT |  | 1
16 | BAY MARSHALLING KIOSK (2 nos on 220 kV bay, 03 Nos 132 kv bay ) | NOS |  | 5
17 | SWITCH YARD AC CONSOLE FOR LIGHTING (01 nos on 220 kV bay, 01 Nos 132 kv bay ) | NOS |  | 2
18 | SWITCH YARD RECEPTACLE BOARD FOR TFR OIL FILTERATION (01 no. near 220/132 KV Auto Tfr ,) | NOS |  | 1
19 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY (01 nos on 220 kV bay, 02 Nos 132 kv bay ) | NOS |  | 3
20 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220/132/33 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS
20.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
20.1.1 | P1S-220 KV (NOMINAL UNIT WT- 4.5 MT) | NOS | 4.5 | 17
20.1.2 | P2S-220 KV (NOMINAL UNIT WT- 4.5 MT) | NOS | 4.5 | 2
20.1.3 | T1S - 132 KV(NOMINAL UNIT WT- 1.2 MT) | NOS | 1.2 | 20
20.1.4 | T4S - 132KV (NOMINAL UNIT WT- 0.95 MT) | NOS | 0.95 | 5
20.1.5 | T8S - 33KV(NOMINAL UNIT WT- 0.8 MT) | NOS | 0.8 | 0
20.1.6 | T9S - 33KV(NOMINAL UNIT WT- 0.6 MT) | NOS | 0.6 | 0
20.1.7 | 220 KV D/C-OC type (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.839 MT, HEIGHT: 35.645 mtrs,BASE:10.8 mtrs) | NOS | 9.839 | 1
20.2 | DIFFERENT TYPE OF BEAMS WITH DETAILS
20.2.1 | Q1S-220KV (NOMINAL UNIT WT- 1.5 MT) | NOS | 1.5 | 14
20.2.2 | G1 - 132 KV(NOMINAL UNIT WT- 0.62 MT) | NOS | 0.62 | 17
20.2.3 | G1X - 132 KV (NOMINAL UNIT WT- 1.4 MT) | NOS | 1.4 | 0
20.2.4 | G2 - 132 KV(NOMINAL UNIT WT- 0.91 MT) | NOS | 0.91 | 4
20.2.5 | G1,2 - 132 KV(Each two beams of G1 type) (NOMINAL UNIT WT- 1.25 MT) | NOS | 1.25 | 0
20.2.6 | G6 - 33KV (NOMINAL UNIT WT- 0.53 MT) | NOS | 0.53 | 0
20.2.7 | G4 - 33KV(NOMINAL UNIT WT- 0.4 MT) | NOS | 0.4 | 0
20.2.8 | G4X - 33KV (NOMINAL UNIT WT- 0.4 MT) | NOS | 0.4 | 0
20.2.9 | TOTAL WEIGHT OF COLUMN & BEAM | MT |  | 159.269
20.3 | SUPPORT STRUCTURES (LATTICE/PIPE TYPE) FOR ALL 220KV, 132 KV & 33KV EQUIPMENTS
20.3.1 | ISOLATORS-220KV | SET | 0.725 | 8
20.3.2 | ISOLATORS-132KV | SET | 1.16 | 12
20.3.3 | ISOLATORS-33 KV | SET | 0.71 | 0
20.3.4 | CTS-220 KV | SET | 0.254 | 6
20.3.5 | CTS-132 KV | SET | 0.226 | 15
20.3.6 | CTS-33 KV | SET | 0.181 | 0
20.3.7 | CVTS-220 KV | SET | 0.254 | 0
20.3.8 | CVTS-132 KV | SET | 0.246 | 6
20.3.9 | IVTS-220 KV | SET | 0.254 | 0
20.3.10 | IVTS-132 KV | SET | 0.246 | 3
20.3.11 | IVTS-33 KV | SET | 0.134 | 0
20.3.12 | Surge Arrester-220 Kv | SET | 0.254 | 6
20.3.13 | Surge Arrester-132 kV | SET | 0.226 | 12
20.3.14 | Surge Arrester-33 kV | SET | 0.181 | 0
20.3.15 | Wave Trap-220 KV | SET | 0.254 | 0
20.3.16 | Wave Trap-132 KV | SET | 0.246 | 4
20.3.17 | BPI-220 KV | SET | 0.254 | 14
20.3.18 | BPI-132 KV | SET | 0.226 | 18
20.3.19 | BPI-33 KV | SET | 0.134 | 0
20.3.20 | NCTS | SET | 0.226 | 2
20.3.21 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT |  | 40.144
20.4 | TOTAL WEIGHT OF COLUMN & BEAM AND SUPPORT STRUCTURE FOR ABOVE EQUIPMENT(22.2.9+22.3.21) | MT |  | 199.413
20.5 | Total weight of GI Nuts and bolts for the above structures(@10% of Total structure weight) | MT |  | 19
20.6 | ANY OTHER STRUCTURES IF REQUIRED WITH DETAILS | MT |  | 1
21 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
21.1 | POWER CABLES,1.1KV,XLPE,ARMOURED, ALUMINIUM CONDUCTOR (As per Specification)
21.1.1 | 3.5 CX185 mm2 | KMS |  | 1
21.1.2 | 3.5 CX120 mm2 | KMS |  | 1
21.1.3 | 3.5 CX70 mm2 | KMS |  | 1
21.1.4 | 3.5 CX35 mm2 | KMS |  | 1
21.1.5 | 4 CX 16 mm2 | KMS |  | 5
21.1.6 | 4 CX 6 mm2 | KMS |  | 5
21.1.7 | 2CX 6 mm2 | KMS |  | 4
21.2 | CONTROL CABLES,1.1 KV, PVC,STRANDED COPPER(As per specification)
21.2.1 | 4 CX 2.5 mm2 | KMS |  | 28
21.2.2 | 5 CX 2.5 mm2 | KMS |  | 25
21.2.3 | 7CX 2.5 mm2 | KMS |  | 15
21.2.4 | 10 CX 2.5 mm2 | KMS |  | 20
21.2.5 | 12 CX 2.5 mm2 | KMS |  | 5
21.2.6 | 16 CX 2.5 mm2 | KMS |  | 2
21.2.7 | 19 CX 2.5 mm2 | KMS |  | 4
21.3 | Perforated G.I Cable trays(2mm thickness) with accessories for laying of cables in cable trench of different section(1-1;2-2;3-3;4-4) as per T.S. | LOT |  | 1
21.4 | ACCESSORIES FOR PLCC SYSTEM AS PER TECHNICAL SPECIFICATION
21.4.1 | 132 kV Line Trap for Pedestal mounting with complete accessories :800A, 0.5 mH, (90-500kHZ),Isc=40kA compatible to IEC 353 specifications | NOS |  | 4
21.4.2 | LINE MATCHING UNIT & LINE MATCHING DISTRIBUTION UNIT | SET |  | 2
21.4.3 | 12.5 mm OD armoured Co-axial Cable; Impedance: 75 ohms, Insulation Resistance: 100 Meg Ohms Dielectric strengh: 5 kV, Signal attenuation: 6 dB/KM (Max) at 500 kHz | MTRS |  | 1000
21.4.4 | 25 PAIR ARMOURED JELLY FILLED CABLE | MTRS |  | 500
21.4.5 | 10 PAIR ARMOURED TELEPHONE CABLES | MTRS |  | 250
21.4.6 | 4 PAIR NON ARMOURED TELEPHONE CABLES | MTRS |  | 100
22 | SUB-STATION SWITCH YARD LIGHTING
23 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS)(includes Switc yard)
23.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,Cables,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | LOT |  | 1
24 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16-ANNEXURE - I)
24.1 | FOAM TYPE-9 LTRS | NOS |  | 2
24.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS |  | 2
24.3 | DRY POWDER TYPE - 5 KGS | NOS |  | 2
24.4 | CO2 - 4.5 KGS | NOS |  | 5
24.5 | CO2 - 9 KGS | NOS |  | 5
24.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS |  | 4
24.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND | SET |  | 4
25 | PROTECTION,CONTROL METERING, EVENT LOGGER,BUS BAR PROTN PAN,COMM PAN, RELAY TOOL KITS AS PER TECH SPEC
25.1 | 220 KV SIDE
25.1.1 | TRANSFORMER CONTROL PANEL(CPL-2D) | NOS |  | 2
25.1.2 | TRANSFORMER RELAY PANEL(RPL-2D) | NOS |  | 2
25.1.3 | 220 KV BUS BAR MODULE SUITABLE FOR EXISTING BUS-BAR RELAY PANEL(RBB-2D)(To be matched with the existing Bus Bar protection scheme. Existing Bus Bsr is of Siemens make,Distributed type. Only Bay module to be provided and to be connected to the Master unit through Optical Fiber cable)(220 KV Bay extension for 2 Nos Auto Transformer) | NOS |  | 2
25.1.4 | 220 KV PAS MODULE SUITABLE FOR EXISTING AUTOMATION PANEL(To be matched with the existing Automation scheme. Existing S/S Automation is of Siemens make,.Only Bay module to be provided and to be connected to the Master unit through Optical Fibre cable)(220 KV Bay extension for 2 Nos Auto Transformer) | NOS |  | 2
25.2 | 132 KV SIDE
25.2.1 | FEEDER CONTROL PANEL(CPF-1M) | NOS |  | 2
25.2.2 | TRANSFORMER CONTROL PANEL(CPL-1M)(2 for 132 KV Side of 220/132/33 KV Auto Tfr ) | NOS |  | 2
25.2.3 | BUSCOUPLER CONTROL PANEL (CPB-1M) | NOS |  | 1
25.2.4 | FEEDER RELAY PANEL(RPF-1M) | NOS |  | 2
25.2.5 | TRANSFORMER RELAY PANEL(RPL-1M), 02 NOS FOR 220/132 KV AUTO TRANSFORMERS ON 132 KV SIDE | NOS |  | 2
25.2.6 | BUSCOUPLER RELAY PANEL (RPB-1M) | NOS |  | 1
25.2.7 | COMMON PANEL (KP-1) | NOS |  | 1
26 | AC & DC SYSTEM
26.1 | AC SYSTEM
26.1.1 | ACDB (HAVING 400A MCCB) AS PER SPECIFICATION (AC DB-1,AC DB-2 WITH B/C) | SET |  | 1
26.2 | DC SYSTEM
26.2.1 | 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C) | SET |  | 1
27 | DISTLED WATER PLANT OF 10 LTR/HR FOR BATTERY BANKS | SET |  | 1
28 | WALKIE TALKIE SET | SET/PAIR |  | 2
29 | PEDESTAL MOUNTED WHEEL FITTED DERRICK FOR LIFTING/ LOWERING OF MATERIALS UP TO 1.5 TON CAPACITY.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 20) | SET |  | 1
30 | POWER WINCH NEAR STORE SHED FOR HANDLING MATERIALS UPTO 5 TON CAPACITY. | SET |  | 1
31 | BEST QUALITY & APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT & BACK SIDE (where doors of the panels are provided) OF ALL PANELS,BOARDS ETC. | LOT |  | 1
32 | ERECTION OF PLCC EQUIPMENT SUPPLIED BY OWNER INCLUDING DISMANTLING FROM EXISTING SUBSTATION ( AS PER THE DETAILS SLD GIVEN IN TS) AND TRANSPORTATION AS REQUIRED | LOT |  | 1
33 | RECEIVING THE TRANSFORMERS AND ITS ACCESSORIES FROM NEAREST OPTCL STORES,DRAGGING AND INSTALLING ON THE PLINTH AND PLACING IN POSITION, ERECTION OF ACCESSORIES OF THE TRANSFORMERS, EART-HING AS PER STANDARD(INCLUDING SUPPLY OF MATERIALS),VACUUM TREATMENT OF THE TANK AND WINDING,OIL FILTRATION(INCLUDING SUPPLY OF VACUUM CUM OIL FILTER MACHINE),SUPPLY & LAYING OF ALL TYPES OF CONTROL & POWER CABLES PERTAINING TO TRANSFORMERS ,TESTING AND COMMISSIONING INCLUDING ALL TESTS OF THE OILS AS PER STIPULATION IN THE STANDARD APPROVED TESTING LABORATORY AND AS PER THE INSTRUCTION OF THE ENGINEER IN CHARGE.THIS INCLUDE ALL RELATED WORKS FOR ERECTION(Transformer and its accessories,RTCC Panel etc),TESTING AND COMMISSIONING OF THE POWER TRANSFORMERS.(CONTRACTOR TO ARRANGE POWER SUPPLY FOR FILTRATION AND VACUUM TREATMENT WORKS).IT ALSO INCLUDES SUPPLY OF ALL MATERIALS FOR ERECTTION INCLUDING T&P's. 1. 220/132/33 KV 160/100 MVA: 02 Nos | NOS |  | 2
TOTAL of Part-I (A) (ELECTRICAL WORKS)
B | CIVIL WORKS
1 | Foundations : Design, engineering, supply of all labour, material (Cement-OPC-43 Grade,MS Rod, coarse and fine aggregates(Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation,concreting, shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal structures and equipment support & others as per the technical specification and approved drawings.(RCC RATIO 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge.
1.1 | Switch yard gantry/portal structure foundations.(Bidders may identify the numbers and type of structures for each type of switch yard and indicate the same along with the erection price
a | P1S | Nos |  | 17
b | P2S | Nos |  | 2
c | T1S | Nos |  | 20
d | T4S | Nos |  | 5
e | OC TYPE TOWER | NOS |  | 1
1.2 | Equipment foundations :
1.2.1 | 245kV circuit breaker | Nos |  | 2
1.2.2 | (a) 245 KV Isolator (S/I)( W E/S & W/O E/S) | Nos |  | 4
| (b) 245kV isolators (tandem type) | Nos |  | 4
1.2.3 | 245kV current transformers | Nos |  | 6
1.2.4 | 216kV Surge arrestors | Nos |  | 6
1.2.5 | 245kV bus post Insulators | Nos |  | 14
1.2.6 | 145kV circuit breaker | Nos |  | 5
1.2.7 | (a) 145 KV Isolators (S/I) | Nos |  | 8
| (b) 145kV isolators (D/I)(W E/S & W/O E/S) | Nos |  | 4
1.2.8 | 145kV current transformers | Nos |  | 15
1.2.9 | a)145kV capacitor voltage transformers | Nos |  | 6
| b)145 KV IVT | Nos |  | 3
1.2.10 | 120kV surge arrestors | Nos |  | 12
1.2.11 | 145kV bus post Insulators | Nos |  | 18
1.2.12 | 145kV line traps (pedestal mounted) | Nos |  | 4
1.2.13 | BAY MARSHALLING KIOSK (2 nos on 220 kV bay, 03 Nos 132 kv bay ) | NOS |  | 5
1.2.14 | SWITCH YARD AC CONSOLE FOR LIGHTING (01 nos on 220 kV bay, 01 Nos 132 kv bay ) | NOS |  | 2
1.2.15 | SWITCH YARD RECEPTACLE BOARD FOR TFR OIL FILTERATION (01 no. near 220/132 KV Auto Tfr ,) | NOS |  | 1
1.2.16 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY (01 nos on 220 kV bay, 02 Nos 132 kv bay ) | NOS |  | 3
1.2.17 | NCT FOUNDATIONS near Transformers as per the direction of Engineer In charge. | NOS |  | 2
1.3 | Excavation: in all types of soil or rocks, back filling including borrowed earth if required ,and disposal of excess earth as per the direction of Engineer In charge as required for the above foundations.
1.3.1 | Soft/Loose Soil | Cum |  | 900
1.3.2 | Soft Rock | Cum |  | 2400
1.4 | Concreting with cost of cement & without Steel as required for the above foundations
1.4.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum |  | 250
1.4.2 | Open cast foundation for the above column/equipment/marshalling box foundations { Sl No. 1.1 & 1.2} with RCC: 1:1.5:3 (Grade M-20),including supply of Labour all materials like Steel (Supply,Cutting,Bending,Binding (including supply of binding wire) and placing in position of steel rods of different size as per design in the foundation pit as required for the above foundations),Cement, coarse and fine aggregates,shuttering,proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. | Cum |  | 1310
2 | Cable Trenches: Design, engineering, and construction of RCC(1:1.5:3) cable trenches and all associated works for cable trench crossings to the required depths, precast RCC covers(1:1.5:3), water stops, brickwork with plastering wherever required including the supply of labour,material, cement, reinforcement steel, form work, steel angles(G.I), flats(G.I) and providing PCC(1:3:6) below cable trenches as per technical specifications and approved drawings and as per direction of the Project Manager. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. *CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE(Duly painted as per instruction of Engg in charge) INCLUDING STANDARD SUPPORT STAND(M.S JOIST ,CHANNEL,ANGLE).
2.1 | Cable trench with covers
2.1.1 | Section 1-1 | Mtrs |  | 200
2.1.2 | Section 2- 2 | Mtrs |  | 100
2.1.3 | Section 3-3 | Mtrs |  | 100
2.1.4 | Section 4-4 | Mtrs |  | 150
2.2 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,formwork etc,and all associated works for construction of trench crossing as per technical specification and approved drawing.
2.2.1 | Road crossing for
2.2.2 | Section 1-1 | Lot |  | 1
2.2.3 | Section 2- 2 | Lot |  | 1
2.2.4 | Section 3-3 | Lot |  | 1
3 | Switch yard buildings: Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawings and specification.
3.1 | CONTROL ROOM BUILDING:(one building) A) Area of the Ground floor with portico at front side, stair case to first floor and top of the building , and a ramp(for 220/132 KV S/S) at the backside for easy transportation of panels to the control room to be located at the first floor. The details of rooms to be provided are as per the Tech spec. B) Area of the first floor. The details of rooms to be provided are as per the Tech spec. Size of Ground floor. Nos./ area of ground floor/area of first floor . 01 No/ Area of Ground Floor 50mtrsX25mtrs (1250sq mtrs) / Area of first floor 25mtrsX25mtrs (625 sq mtrs)
4 | Roads: Design, construction of roads and walkways/ shoulders within sub-station(Switch yard area,colony area,approach road,control room building area, main gate to the switch yard gate etc) as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Engineer In charge. Provision of drains on both the side of the roads for easy discharge of rain water.
4.1 | 7.0 mtrs concrete road in front of the Transformer as per technical specification indicated in the civil section(from the switch yard main gate& drain at both side of the road, as per the instruction of Engineer in Charge. | Lots |  | 1
4.2 | 3.75 mtrs Bituminus road with soulder at both the side & shall have drain on both side of the road as per technical specification indicated in the civil section( Periphery roads outside switch yard fencing and colony roads) | Lots |  | 1
4.3 | 7 mtrs wide Bituminus roads with shoulder as per specification indicated in the civil section.( for main and approach roads).Shall have drain on both side of the road. | Lots |  | 1
5 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme, road-culverts, and drains crossing cable trenches etc. as per specification and approved drawing.This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge.All the switcyard bays , roads water drainage shall be connected to the mainsurface drain.As per approved drawing and specification.
5.1 | Storm water drain | Lots |  | 1
5.2 | Road-culverts, drain crossings | Lots |  | 1
5.3 | Cable trench crossing | Lots |  | 1
6 | Foundations for transformers :Design, engineering, supply of labour, material, equipments and construction of Auto-transformer/Transformer foundation including piling if any, all associated works, rail tracks, jacking pads,anchor block RCC and PCC, miscellaneous structural steel including oil collection pits, MS grating(if required), gravel filling, and other items etc. not mentioned herein, but specifically required for the completion of the work as per technical specification and approved drawing. (Rate shall be inclusive of cement, reinforcement steel, angles,flats and form work etc.)(all cement concrete shall have RCC ratio 1:1.5:3). Transformer RCC foundation and Rail Track should be extended upto the approaching road (However,the height of RCC foundation beyond transformer main plinth area should be same as height of concrete road as per item under 4.1). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. 1. 220/132 KV, 160 MVA : (2 Nos)
6.1 | 160 MVA,100 MVA, 220/ 132kV transformers a) Overall dimension of transformer(appox) Length:11500 mmX Width 7000 mmX Height 7500 mm b) Total weight with oil and tank: 195 MT (appox) | Nos |  | 2
6.2 | OIL SUMP PIT:Oil collection (from transformers)sump pit with provision of pump(5 HP, with auto level control , including cabling, fixing of control gear )as per CIGRE. As per spec and approved drawing. >Oil capacity of each Transformer in ltrs appox. a) 160 MVA,220/132/33 KV: 68000 ltrs. b) 20/40 MVA,132/33 KV: 26500 ltrs. c) 40 MVA,220/33 KV : 36000 ltrs. (1 for Auto Tfr + 1 for power Tfr) | Nos |  | 1
7 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area .Proper leveling of the switch yard area, anti-weed treatment, spreading of plain cement concrete with mixing ratio 1:4:8 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area . As per technical specification and approved drawing, and as per the instruction of the Engineer-in-Charge. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. | Lots |  | 1
8 | Metal Spreading:Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8).The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | Lots |  | 1
9 | Levelling of sub-station and other area.
9.1 | LEVELLING OF S/S AREA:Providing, neatly dressing up and leveling of substation area including switch yard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification.
9.2 | Contour survey of the entire sub-station area including Supply of all labour & T&P by contractor. | SQM |  | 15000
9.3 | Cutting of sub-station area of the as per the direction of Engineer in Charge. | Cum |  | 5000
9.4 | Filling with borrowed earth beyond 30 mtrs lead as per the direction of Engineer in Charge. | Cum |  | 10000
10 | Switch yard fencing: Providing and fixing of G.I Goat mesh (2.5 mm dia) fencing( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, state and central government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Brick masonry work with ratio 1:5 and cement pointing of the joints, for the fencing up to a height from the finished ground level) .This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing as per specification. | MTRS |  | 525
11 | Fire wall: Design, engineering, procurement of labour, material including all associated works for construction of fire-walls as per technical specification and approved drawings(column shall be RCC ratio1:1.5:3 and the walls are of fire resistant bricks).This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. Painting of the walls as per direction of the Engineer in charge. | Lots |  | 1
12 | Any other civil work to be included in the schedule by the Bidder if required essential for successful completion of project, including supply of labour, material, cement reinforcement steel, form work etc. Bidder shall also quote the unit rate for the following items of works.(Rate shall be inclusive of supply of labour, material, cement, reinforcement steel, form work etc. )
12.1 | Excavation This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Engineer In charge. | Cu.m. |  | 1
12.2 | PCC: M10(1: 3 : 6) | Cu.m. |  | 1
12.3 | RCC M 15(1:2:4) | Cu.m. |  | 1
12.4 | RCC: M 20(1:1.5:3) | Cu.m. |  | 1
12.5 | Brick masonry work in cement sand mortar 1: 6 with bricks of class designation 75. | Cu.m. |  | 1
12.6 | 12 mm thick plaster in cement sand mortar ( 1: 6 ). | Sq.m. |  | 1
12.7 | Cutting,bending,binding(supply of binding wires) and fixing of reinforcement(including supply of reinforcement). | M.T. |  | 1
13 | Switch yard lighting: Design, engineering, procurement of labour, material including all associated works for construction of switch yard lighting as per technical specification and approved drawings. The fixture shall be of reputed make (Philips/CGL/Bajaj) and fixtures shall be of LED lamps and proper cabling from the lighting outdoor distribution boards to the junction boxes and from junction boxes to the fixtures. The lighting fixtures are to be installed on the switch yard structures. The quantity of such fixtures are to be designed and to be ascertained. | Lots |  | 1
14 | MAIN & SWITCH YARD GATES:Design, engineering, procurement of labour, material including all associated works for construction and fixing of of a main gate and one no. switch yard gates with men gates as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. Provision of gate lights (Post top lantern type) on each pillar of the gate. It includes supply & fixing of light fixtures including LED Gate lamp, LV XLPE cables, switchgear etc required to complete works as per specification and approved drawings | Lot |  | 1
15 | COLOUR CODING, BAY MARKING Etc:Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a) Colur coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof snickering may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. MS sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot |  | 1
16 | PROVISION OF RAMP:Design, engineering, procurement of labour, material including all associated works for construction and fixing of Ramp as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. Provision of a ramp of adequate size and capable of for loading and unloading of the materials of 5 Ton capacity from the lorry or to the lorry near the store shed. Adequate size of MS frames and RCC (1:1.5:3) based ramps to be used for the said purpose. | Lot |  | 1
TOTAL OF CIVIL WORKS (B)
GRAND TOTAL ( ELECTRICAL WORKS + CIVIL WORKS) (A+B)
Note:
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested not to leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value). No rate shall be furnished/obtained after bid opening (Ref clause no 33.4.1 of INB vol-I) .
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | Bidder has to quote rates excluding service tax (if any), service tax shall be paid/reimbursed as per conditions of Bid Document.
Date : |  |  |  | (Signature) ……………………………………………
Place : |  |  |  | ( Name) ………………………………………………
( Designation ) ……………………………………….
(Common Seal) ……………………………………

## Schedule 2A SS
ORISSA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2X160 MVA,220/132 Sub-Station along with 132KV Transmission Lines and associated system
At MENDHASAL
Bid Document No. : Sr. G.M-CPC-TENDER-PACKAGE- 61-02 /2012
(Equipment/Materials Price Break-up of Ex-works Prices against PACKAGE 61-02 / 2012 )
PART-I, SCHEDULE-2A (FOR SUBSTATION) |  |  |  |  | PRICE IN INDIAN RUPEES
SL NO | SUPPLY OF FOLLOWING EQUIPMENT (As per Technical Specification) | Unit |  | Quantity for 2X160 MVA,220/132 Substation at MENDHASAL [02 Nos 220 KV TRANSFORMER Bays,7 Nos(2Fdr+2T+1B/C+2 SPARE)132 KV Bays. | Unit Ex-works Price | Total Ex-works Price | Mode of Transaction (Direct or Bought-out item) | Total Taxes & Duties applicable for transaction between bidder and OPTCL and not included in the price at Column(6) [For bought-out items, taxes & duties excluding Octroi/Entry Tax are invariably included in the price quoted at column(6)]
[8 empty] | Excise Duty | Sales Tax | Other Levies(if any)
1 | 2 | 3 |  | 4 | 5 | 6= 4X5 | 7 | 8 | 9 | 10
1 | 245 KV,1200-600-300A,40KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 6
2 | 245 KV,1600A,40KA,ISOLATORS
2.1 | WITH OUT EARTH SWITCH | NOS |  | 2
2.2 | WITH SINGLE EARTH SWITCH | NOS |  | 2
2.3 | TANDEM WITHOUT EARTH SWITCH | NOS |  | 4
3 | 245KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 2
4 | 216 KV, METAL OXIDE SURGE ARRESTOR,10 KA, class III | NOS |  | 6
5 | 220 KV Bus Post Insulators | NOS |  | 14
6 | 145 KV,(Different Ratio),40 KA,4CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 15
7 | 145 KV,1200A,40 KA,ISOLATORS
7.1 | S/I WITH OUT EARTH SWITCH (Includes sectiona switches at the main bus near B/C ) | NOS |  | 8
7.2 | D/I WITH SINGLE EARTH SWITCH | NOS |  | 2
7.3 | D/I WITHOUT EARTH SWITCH | NOS |  | 2
9 | 145 KV, 6000pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS |  | 6
10 | 120 KV METAL OXIDE SURGE ARRESTOR, 10 KA, Class III | NOS |  | 12
11 | 145 KV ,2 CORE,SINGLE PHASE,IVT | NOS |  | 3
12 | 132 KV Bus Post Insulators | NOS |  | 18
13 | 145KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 5
14 | 36 KV CLASS NCT FOR TRANSFORMER PROTECTION RATING AS DECIDED (RATINGS AS PER THE SUITABILITY) HAVING TWO CORE (IN EACH AUTO TRANSFORMER 1 No. NCT ) | NOS |  | 2
15 | BUS BAR & CIRCUIT MATERIALS
15.1 | FOLLOWING ANTI FOG TYPE DISC INSULATORS
15.1.1 | 160 kN INSULATOR STRINGS for twin Moose cond ( TENSION)-220 KV | SET |  | 24
15.1.2 | 160 kN INSULATOR STRINGS for single Moose cond (TENSION)-220 KV | SET |  | 48
15.1.3 | 120 kN INSULATOR STRINGS for Double Moose cond (TENSION)-132 KV | SET |  | 18
15.1.4 | 120 kN INSULATOR STRINGS for Single Moose cond( TENSION)-132 KV | SET |  | 54
15.1.5 | 90 kN INSULATOR STRINGS for Double/ Single Moose cond ( SUSPENSION)-220 KV | SET |  | 36
15.1.6 | 90 kN INSULATOR STRINGS for Double/ Single Moose cond ( SUSPENSION)-132 KV | SET |  | 24
15.2 | ACSR MOOSE CONDUCTOR | LOT |  | 1
15.3 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | LOT |  | 1
15.4 | EARTH WIRES & IT'S HARDWARES & FITTING, with copper earth bond | LOT |  | 1
16 | SUBSTATION SYSTEMS
16.1 | EARTHING CONDUCTOR FOR BURRIAL : 40 mm DIA MS ROD for laying (spacing maximum 5m) | LOT |  | 1
16.2 | EARTHING CONDUCTOR: 75x10mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | LOT |  | 1
16.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | LOT |  | 1
16.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | LOT |  | 1
17 | BAY MARSHALLING KIOSK (2 nos on 220 kV bay, 03 Nos 132 kv bay ) | NOS |  | 5
18 | SWITCH YARD AC CONSOLE FOR LIGHTING (01 nos on 220 kV bay, 01 Nos 132 kv bay ) | NOS |  | 2
19 | SWITCH YARD RECEPTACLE BOARD FOR TFR OIL FILTERATION (01 no. near 220/132 KV Auto Tfr ,) | NOS |  | 1
20 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY (01 nos on 220 kV bay, 02 Nos 132 kv bay ) | NOS |  | 3
21 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220/132/33 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS
21.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
21.1.1 | P1S-220 KV (NOMINAL UNIT WT- 4.5 MT) | NOS | 4.5 | 17
21.1.2 | P2S-220 KV (NOMINAL UNIT WT- 4.5 MT) | NOS | 4.5 | 2
21.1.3 | T1S - 132 KV(NOMINAL UNIT WT- 1.2 MT) | NOS | 1.2 | 20
21.1.4 | T4S - 132KV (NOMINAL UNIT WT- 0.95 MT) | NOS | 0.95 | 5
21.1.5 | T8S - 33KV(NOMINAL UNIT WT- 0.8 MT) | NOS | 0.8 | 0
21.1.6 | T9S - 33KV(NOMINAL UNIT WT- 0.6 MT) | NOS | 0.6 | 0
21.1.7 | 220 KV D/C-OC type (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.839 MT, HEIGHT: 35.645 mtrs,BASE:10.8 mtrs) | NOS | 9.839 | 1
22.2 | DIFFERENT TYPE OF BEAMS WITH DETAILS
22.2.1 | Q1S-220KV (NOMINAL UNIT WT- 1.5 MT) | NOS | 1.5 | 14
22.2.2 | G1 - 132 KV(NOMINAL UNIT WT- 0.62 MT) | NOS | 0.62 | 17
22.2.3 | G1X - 132 KV (NOMINAL UNIT WT- 1.4 MT) | NOS | 1.4 | 0
22.2.4 | G2 - 132 KV(NOMINAL UNIT WT- 0.91 MT) | NOS | 0.91 | 4
22.2.5 | G1,2 - 132 KV(Each two beams of G1 type) (NOMINAL UNIT WT- 1.25 MT) | NOS | 1.25 | 0
22.2.6 | G6 - 33KV (NOMINAL UNIT WT- 0.53 MT) | NOS | 0.53 | 0
22.2.7 | G4 - 33KV(NOMINAL UNIT WT- 0.4 MT) | NOS | 0.4 | 0
22.2.8 | G4X - 33KV (NOMINAL UNIT WT- 0.4 MT) | NOS | 0.4 | 0
22.2.9 | TOTAL WEIGHT OF COLUMN & BEAM | MT |  | 159.269
22.3 | SUPPORT STRUCTURES (LATTICE/PIPE TYPE) FOR ALL 220KV, 132 KV & 33KV EQUIPMENTS
22.3.1 | ISOLATORS-220KV | SET | 0.725 | 8
22.3.2 | ISOLATORS-132KV | SET | 1.16 | 12
22.3.3 | ISOLATORS-33 KV | SET | 0.71 | 0
22.3.4 | CTS-220 KV | SET | 0.254 | 6
22.3.5 | CTS-132 KV | SET | 0.226 | 15
22.3.6 | CTS-33 KV | SET | 0.181 | 0
22.3.7 | CVTS-220 KV | SET | 0.254 | 0
22.3.8 | CVTS-132 KV | SET | 0.246 | 6
22.3.9 | IVTS-220 KV | SET | 0.254 | 0
22.3.10 | IVTS-132 KV | SET | 0.246 | 3
22.3.11 | IVTS-33 KV | SET | 0.134 | 0
22.3.12 | Surge Arrester-220 Kv | SET | 0.254 | 6
22.3.13 | Surge Arrester-132 kV | SET | 0.226 | 12
22.3.14 | Surge Arrester-33 kV | SET | 0.181 | 0
22.3.15 | Wave Trap-220 KV | SET | 0.254 | 0
22.3.16 | Wave Trap-132 KV | SET | 0.246 | 4
22.3.17 | BPI-220 KV | SET | 0.254 | 14
22.3.18 | BPI-132 KV | SET | 0.226 | 18
22.3.19 | BPI-33 KV | SET | 0.134 | 0
22.3.20 | NCTS | SET | 0.226 | 2
22.3.21 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT |  | 40.144
22.4 | TOTAL WEIGHT OF COLUMN & BEAM AND SUPPORT STRUCTURE FOR ABOVE EQUIPMENT(22.2.9+22.3.21) | MT |  | 199.413
22.5 | Total weight of GI Nuts and bolts for the above structures(@10% of Total structure weight) | MT |  | 19
22.6 | ANY OTHER STRUCTURES IF REQUIRED WITH DETAILS | MT |  | 1
23 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
23.1 | POWER CABLES,1.1KV,XLPE,ARMOURED, ALUMINIUM CONDUCTOR (As per Specification)
23.1.1 | 3.5 CX185 mm2 | KMS |  | 1
23.1.2 | 3.5 CX120 mm2 | KMS |  | 1
23.1.3 | 3.5 CX70 mm2 | KMS |  | 1
23.1.4 | 3.5 CX35 mm2 | KMS |  | 1
23.1.5 | 4 CX 16 mm2 | KMS |  | 5
23.1.6 | 4 CX 6 mm2 | KMS |  | 5
23.1.7 | 2CX 6 mm2 | KMS |  | 4
23.2 | CONTROL CABLES,1.1 KV, PVC,STRANDED COPPER(As per specification)
23.2.1 | 4 CX 2.5 mm2 | KMS |  | 28
23.2.2 | 5 CX 2.5 mm2 | KMS |  | 25
23.2.3 | 7CX 2.5 mm2 | KMS |  | 15
23.2.4 | 10 CX 2.5 mm2 | KMS |  | 20
23.2.5 | 12 CX 2.5 mm2 | KMS |  | 5
23.2.6 | 16 CX 2.5 mm2 | KMS |  | 2
23.2.7 | 19 CX 2.5 mm2 | KMS |  | 4
23.3 | Perforated G.I Cable trays(2mm thickness) with accessories for laying of cables in cable trench of different section(1-1;2-2;3-3;4-4) as per T.S. | LOT |  | 1
23.4 | ACCESSORIES FOR PLCC SYSTEM AS PER TECHNICAL SPECIFICATION
23.4.1 | 132 kV Line Trap for Pedestal mounting with complete accessories :800A, 0.5 mH, (90-500kHZ),Isc=40kA compatible to IEC 353 specifications | NOS |  | 4
23.4.2 | LINE MATCHING UNIT & LINE MATCHING DISTRIBUTION UNIT | SET |  | 2
23.4.3 | 12.5 mm OD armoured Co-axial Cable; Impedance: 75 ohms, Insulation Resistance: 100 Meg Ohms Dielectric strengh: 5 kV, Signal attenuation: 6 dB/KM (Max) at 500 kHz | MTRS |  | 1000
23.4.4 | 25 PAIR ARMOURED JELLY FILLED CABLE | MTRS |  | 500
23.4.5 | 10 PAIR ARMOURED TELEPHONE CABLES | MTRS |  | 250
23.4.6 | 4 PAIR NON ARMOURED TELEPHONE CABLES | MTRS |  | 100
24 | SUB-STATION SWITCH YARD LIGHTING
25 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS)(includes Switc yard)
25.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,Cables,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | LOT |  | 1
26 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16-ANNEXURE - I)
26.1 | FOAM TYPE-9 LTRS | NOS |  | 2
26.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS |  | 2
26.3 | DRY POWDER TYPE - 5 KGS | NOS |  | 2
26.4 | CO2 - 4.5 KGS | NOS |  | 5
26.5 | CO2 - 9 KGS | NOS |  | 5
26.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS |  | 4
26.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND | SET |  | 4
27 | PROTECTION,CONTROL METERING, EVENT LOGGER,BUS BAR PROTN PAN,COMM PAN, RELAY TOOL KITS AS PER TECH SPEC
27.1 | 220 KV SIDE
27.1.1 | TRANSFORMER CONTROL PANEL(CPL-2D) | NOS |  | 2
27.1.2 | TRANSFORMER RELAY PANEL(RPL-2D) | NOS |  | 2
27.1.3 | 220 KV BUS BAR MODULE SUITABLE FOR EXISTING BUS-BAR RELAY PANEL(RBB-2D)(To be matched with the existing Bus Bar protection scheme. Existing Bus Bsr is of Siemens make,Distributed type. Only Bay module to be provided and to be connected to the Master unit through Optical Fiber cable)(220 KV Bay extension for 2 Nos Auto Transformer) | NOS |  | 2
27.1.4 | 220 KV PAS MODULE SUITABLE FOR EXISTING AUTOMATION PANEL(To be matched with the existing Automation scheme.Existing S/S Automation is of Siemens make,.Only Bay module to be provided and to be connected to the Master unit through Optical Fibre cable)(220 KV Bay extension for 2 Nos Auto Transformer) | NOS |  | 2
27.2 | 132 KV SIDE
27.2.1 | FEEDER CONTROL PANEL(CPF-1M) | NOS |  | 2
27.2.2 | TRANSFORMER CONTROL PANEL(CPL-1M)(2 for 132 KV Side of 220/132/33 KV Auto Tfr ) | NOS |  | 2
27.2.3 | BUSCOUPLER CONTROL PANEL (CPB-1M) | NOS |  | 1
27.2.4 | FEEDER RELAY PANEL(RPF-1M) | NOS |  | 2
27.2.5 | TRANSFORMER RELAY PANEL(RPL-1M), 02 NOS FOR 220/132 KV AUTO TRANSFORMERS ON 132 KV SIDE | NOS |  | 2
27.2.6 | BUSCOUPLER RELAY PANEL (RPB-1M) | NOS |  | 1
27.2.7 | COMMON PANEL (KP-1) | NOS |  | 1
28 | AC & DC SYSTEM
28.1 | AC SYSTEM
28.1.1 | ACDB (HAVING 400A MCCB) AS PER SPECIFICATION (AC DB-1,AC DB-2 WITH B/C) | SET |  | 1
28.2 | DC SYSTEM
28.2.1 | 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C) | SET |  | 1
23 | DISTLED WATER PLANT OF 10 LTR/HR FOR BATTERY BANKS | SET |  | 1
24 | WALKIE TALKIE SET | SET /PAIR |  | 2
25 | PORTABLE ALUMINIUM LADDER EXTENDABLE TYPE OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT INSIDE SWITCH YARD.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 19) | NOS |  | 1
26 | PEDESTAL MOUNTED WHEEL FITTED DERRICK FOR LIFTING/ LOWERING OF MATERIALS UP TO 1.5 TON CAPACITY.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 20) | SET |  | 1
27 | POWER WINCH NEAR STORE SHED FOR HANDLING MATERIALS UPTO 5 TON CAPACITY. | SET |  | 1
28 | MAINTENANCE TESTING EQUIPMENT (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 17 ANNEXURE - II ,INDICATED IN -SCHEDULE OF REQUIREMENTS OF MAINTENANCE EQUIPMENT) | LOT |  | 1
29 | OTHER TOOLS AND PLANTS (T&P's) REQUIREMENT (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 18 ANNEXURE - III ,INDICATED IN SCHEDULE OF REQUIREMENTS OTHER T&P's) | LOT |  | 1
30 | OFFICE FURNITURE (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 18 ANNEXURE - IV ,INDICATED IN SCHEDULE OF REQUIREMENTS OFFICE FURNITURE) & PLACING IN CONTROL ROOM,CONFERENCE ROOM,OFFICE ROOMS,LIBRARY,TESTING LAB,etc. | LOT |  | 1
31 | BEST QUALITY & APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT & BACK SIDE (where doors of the panels are provided) OF ALL PANELS,BOARDS ETC. | LOT |  | 1
TOTAL OF SUBSTATION-2A(SUPPLY) (PART-I)
Note:
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested not to leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value). No rate shall be furnished/obtained after bid opening (Ref clause no 33.4.1 of INB vol-I)
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | In mode of transaction column please indicate Direct/Bought-Out. For Taxes & Duties on Direct/Bought-out items ref clause 6.0 of SCC (Vol-IA)
| Date : | (Signature) ……………………………………………
| Place : | ( Name) ………………………………………………
( Designation ) ……………………………………….
(Common Seal) ……………………………………

## Schedule 2B SS
ORISSA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2X160 MVA,220/132 Sub-Station along with 132KV Transmission Lines and associated system
At MENDHASAL
Bid Document No. : Sr. G.M-CPC-TENDER-PACKAGE- 61-02 /2012
(Equipment/Materials Price Break-up of Ex-works Prices against PACKAGE 61-02 / 2012 )
PART-I, SCHEDULE-2B (FOR SUBSTATION) |  |  |  |  | PRICE IN INDIAN RUPEES
SL NO | F&I FOR SUPPLY OF FOLLOWING EQUIPMENT (As per Technical Specification) | Unit |  | Quantity for 2X160 MVA,220/132 Substation at MENDHASAL [02 Nos 220 KV TRANSFORMER Bays,7 Nos(2Fdr+2T+1B/C+2 SPARE)132 KV Bays. | Unit F&I Price | Total F&I Price
1 | 2 | 3 |  | 4 | 5 | 6= 4X5
1 | 245 KV,1200-600-300A,40KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 6
2 | 245 KV,1600A,40KA,ISOLATORS
2.1 | WITH OUT EARTH SWITCH | NOS |  | 2
2.2 | WITH SINGLE EARTH SWITCH | NOS |  | 2
2.3 | TANDEM WITHOUT EARTH SWITCH | NOS |  | 4
3 | 245KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 2
4 | 216 KV, METAL OXIDE SURGE ARRESTOR,10 KA, class III | NOS |  | 6
5 | 220 KV Bus Post Insulators | NOS |  | 14
6 | 145 KV,(Different Ratio),40 KA,4CORE SINGLE PHASE CURRENT TRANSFORMER | NOS |  | 15
7 | 145 KV,1200A,40 KA,ISOLATORS
7.1 | S/I WITH OUT EARTH SWITCH (Includes sectiona switches at the main bus near B/C ) | NOS |  | 8
7.2 | D/I WITH SINGLE EARTH SWITCH | NOS |  | 2
7.3 | D/I WITHOUT EARTH SWITCH | NOS |  | 2
9 | 145 KV, 6000pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS |  | 6
10 | 120 KV METAL OXIDE SURGE ARRESTOR, 10 KA, Class III | NOS |  | 12
11 | 145 KV ,2 CORE,SINGLE PHASE,IVT | NOS |  | 3
12 | 132 KV Bus Post Insulators | NOS |  | 18
13 | 145KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS |  | 5
14 | 36 KV CLASS NCT FOR TRANSFORMER PROTECTION RATING AS DECIDED (RATINGS AS PER THE SUITABILITY) HAVING TWO CORE (IN EACH AUTO TRANSFORMER 1 No. NCT ) | NOS |  | 2
15 | BUS BAR & CIRCUIT MATERIALS
15.1 | FOLLOWING ANTI FOG TYPE DISC INSULATORS
15.1.1 | 160 kN INSULATOR STRINGS for twin Moose cond ( TENSION)-220 KV | SET |  | 24
15.1.2 | 160 kN INSULATOR STRINGS for single Moose cond (TENSION)-220 KV | SET |  | 48
15.1.3 | 120 kN INSULATOR STRINGS for Double Moose cond (TENSION)-132 KV | SET |  | 18
15.1.4 | 120 kN INSULATOR STRINGS for Single Moose cond( TENSION)-132 KV | SET |  | 54
15.1.5 | 90 kN INSULATOR STRINGS for Double/ Single Moose cond ( SUSPENSION)-220 KV | SET |  | 36
15.1.6 | 90 kN INSULATOR STRINGS for Double/ Single Moose cond ( SUSPENSION)-132 KV | SET |  | 24
15.2 | ACSR MOOSE CONDUCTOR | LOT |  | 1
15.3 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | LOT |  | 1
15.4 | EARTH WIRES & IT'S HARDWARES & FITTING, with copper earth bond | LOT |  | 1
16 | SUBSTATION SYSTEMS
16.1 | EARTHING CONDUCTOR FOR BURRIAL : 40 mm DIA MS ROD for laying (spacing maximum 5m) | LOT |  | 1
16.2 | EARTHING CONDUCTOR: 75x10mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | LOT |  | 1
16.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | LOT |  | 1
16.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | LOT |  | 1
17 | BAY MARSHALLING KIOSK (2 nos on 220 kV bay, 03 Nos 132 kv bay ) | NOS |  | 5
18 | SWITCH YARD AC CONSOLE FOR LIGHTING (01 nos on 220 kV bay, 01 Nos 132 kv bay ) | NOS |  | 2
19 | SWITCH YARD RECEPTACLE BOARD FOR TFR OIL FILTERATION (01 no. near 220/132 KV Auto Tfr ,) | NOS |  | 1
20 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY (01 nos on 220 kV bay, 02 Nos 132 kv bay ) | NOS |  | 3
21 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220/132/33 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS
21.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
21.1.1 | P1S-220 KV (NOMINAL UNIT WT- 4.5 MT) | NOS | 4.5 | 17
21.1.2 | P2S-220 KV (NOMINAL UNIT WT- 4.5 MT) | NOS | 4.5 | 2
21.1.3 | T1S - 132 KV(NOMINAL UNIT WT- 1.2 MT) | NOS | 1.2 | 20
21.1.4 | T4S - 132KV (NOMINAL UNIT WT- 0.95 MT) | NOS | 0.95 | 5
21.1.5 | T8S - 33KV(NOMINAL UNIT WT- 0.8 MT) | NOS | 0.8 | 0
21.1.6 | T9S - 33KV(NOMINAL UNIT WT- 0.6 MT) | NOS | 0.6 | 0
21.1.7 | 220 KV D/C-OC type (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.839 MT, HEIGHT: 35.645 mtrs,BASE:10.8 mtrs) | NOS | 9.839 | 1
22.2 | DIFFERENT TYPE OF BEAMS WITH DETAILS
22.2.1 | Q1S-220KV (NOMINAL UNIT WT- 1.5 MT) | NOS | 1.5 | 14
22.2.2 | G1 - 132 KV(NOMINAL UNIT WT- 0.62 MT) | NOS | 0.62 | 17
22.2.3 | G1X - 132 KV (NOMINAL UNIT WT- 1.4 MT) | NOS | 1.4 | 0
22.2.4 | G2 - 132 KV(NOMINAL UNIT WT- 0.91 MT) | NOS | 0.91 | 4
22.2.5 | G1,2 - 132 KV(Each two beams of G1 type) (NOMINAL UNIT WT- 1.25 MT) | NOS | 1.25 | 0
22.2.6 | G6 - 33KV (NOMINAL UNIT WT- 0.53 MT) | NOS | 0.53 | 0
22.2.7 | G4 - 33KV(NOMINAL UNIT WT- 0.4 MT) | NOS | 0.4 | 0
22.2.8 | G4X - 33KV (NOMINAL UNIT WT- 0.4 MT) | NOS | 0.4 | 0
22.2.9 | TOTAL WEIGHT OF COLUMN & BEAM | MT |  | 159.269
22.3 | SUPPORT STRUCTURES (LATTICE/PIPE TYPE) FOR ALL 220KV, 132 KV & 33KV EQUIPMENTS
22.3.1 | ISOLATORS-220KV | SET | 0.725 | 8
22.3.2 | ISOLATORS-132KV | SET | 1.16 | 12
22.3.3 | ISOLATORS-33 KV | SET | 0.71 | 0
22.3.4 | CTS-220 KV | SET | 0.254 | 6
22.3.5 | CTS-132 KV | SET | 0.226 | 15
22.3.6 | CTS-33 KV | SET | 0.181 | 0
22.3.7 | CVTS-220 KV | SET | 0.254 | 0
22.3.8 | CVTS-132 KV | SET | 0.246 | 6
22.3.9 | IVTS-220 KV | SET | 0.254 | 0
22.3.10 | IVTS-132 KV | SET | 0.246 | 3
22.3.11 | IVTS-33 KV | SET | 0.134 | 0
22.3.12 | Surge Arrester-220 Kv | SET | 0.254 | 6
22.3.13 | Surge Arrester-132 kV | SET | 0.226 | 12
22.3.14 | Surge Arrester-33 kV | SET | 0.181 | 0
22.3.15 | Wave Trap-220 KV | SET | 0.254 | 0
22.3.16 | Wave Trap-132 KV | SET | 0.246 | 4
22.3.17 | BPI-220 KV | SET | 0.254 | 14
22.3.18 | BPI-132 KV | SET | 0.226 | 18
22.3.19 | BPI-33 KV | SET | 0.134 | 0
22.3.20 | NCTS | SET | 0.226 | 2
22.3.21 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT |  | 40.144
22.4 | TOTAL WEIGHT OF COLUMN & BEAM AND SUPPORT STRUCTURE FOR ABOVE EQUIPMENT(22.2.9+22.3.21) | MT |  | 199.413
22.5 | Total weight of GI Nuts and bolts for the above structures(@10% of Total structure weight) | MT |  | 19
22.6 | ANY OTHER STRUCTURES IF REQUIRED WITH DETAILS | MT |  | 1
23 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
23.1 | POWER CABLES,1.1KV,XLPE,ARMOURED, ALUMINIUM CONDUCTOR (As per Specification)
23.1.1 | 3.5 CX185 mm2 | KMS |  | 1
23.1.2 | 3.5 CX120 mm2 | KMS |  | 1
23.1.3 | 3.5 CX70 mm2 | KMS |  | 1
23.1.4 | 3.5 CX35 mm2 | KMS |  | 1
23.1.5 | 4 CX 16 mm2 | KMS |  | 5
23.1.6 | 4 CX 6 mm2 | KMS |  | 5
23.1.7 | 2CX 6 mm2 | KMS |  | 4
23.2 | CONTROL CABLES,1.1 KV, PVC,STRANDED COPPER(As per specification)
23.2.1 | 4 CX 2.5 mm2 | KMS |  | 28
23.2.2 | 5 CX 2.5 mm2 | KMS |  | 25
23.2.3 | 7CX 2.5 mm2 | KMS |  | 15
23.2.4 | 10 CX 2.5 mm2 | KMS |  | 20
23.2.5 | 12 CX 2.5 mm2 | KMS |  | 5
23.2.6 | 16 CX 2.5 mm2 | KMS |  | 2
23.2.7 | 19 CX 2.5 mm2 | KMS |  | 4
23.3 | Perforated G.I Cable trays(2mm thickness) with accessories for laying of cables in cable trench of different section(1-1;2-2;3-3;4-4) as per T.S. | LOT |  | 1
23.4 | ACCESSORIES FOR PLCC SYSTEM AS PER TECHNICAL SPECIFICATION
23.4.1 | 132 kV Line Trap for Pedestal mounting with complete accessories :800A, 0.5 mH, (90-500kHZ),Isc=40kA compatible to IEC 353 specifications | NOS |  | 4
23.4.2 | LINE MATCHING UNIT & LINE MATCHING DISTRIBUTION UNIT | SET |  | 2
23.4.3 | 12.5 mm OD armoured Co-axial Cable; Impedance: 75 ohms, Insulation Resistance: 100 Meg Ohms Dielectric strengh: 5 kV, Signal attenuation: 6 dB/KM (Max) at 500 kHz | MTRS |  | 1000
23.4.4 | 25 PAIR ARMOURED JELLY FILLED CABLE | MTRS |  | 500
23.4.5 | 10 PAIR ARMOURED TELEPHONE CABLES | MTRS |  | 250
23.4.6 | 4 PAIR NON ARMOURED TELEPHONE CABLES | MTRS |  | 100
24 | SUB-STATION SWITCH YARD LIGHTING
25 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS)(includes Switc yard)
25.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,Cables,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | LOT |  | 1
26 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16-ANNEXURE - I)
26.1 | FOAM TYPE-9 LTRS | NOS |  | 2
26.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS |  | 2
26.3 | DRY POWDER TYPE - 5 KGS | NOS |  | 2
26.4 | CO2 - 4.5 KGS | NOS |  | 5
26.5 | CO2 - 9 KGS | NOS |  | 5
26.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS |  | 4
26.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND | SET |  | 4
27 | PROTECTION,CONTROL METERING, EVENT LOGGER,BUS BAR PROTN PAN,COMM PAN, RELAY TOOL KITS AS PER TECH SPEC
27.1 | 220 KV SIDE
27.1.1 | TRANSFORMER CONTROL PANEL(CPL-2D) | NOS |  | 2
27.1.2 | TRANSFORMER RELAY PANEL(RPL-2D) | NOS |  | 2
27.1.3 | 220 KV BUS BAR MODULE SUITABLE FOR EXISTING BUS-BAR RELAY PANEL(RBB-2D)(To be matched with the existing Bus Bar protection scheme. Existing Bus Bsr is of Siemens make,Distributed type. Only Bay module to be provided and to be connected to the Master unit through Optical Fiber cable)(220 KV Bay extension for 2 Nos Auto Transformer) | NOS |  | 2
27.1.4 | 220 KV PAS MODULE SUITABLE FOR EXISTING AUTOMATION PANEL(To be matched with the existing Automation scheme.Existing S/S Automation is of Siemens make,.Only Bay module to be provided and to be connected to the Master unit through Optical Fibre cable)(220 KV Bay extension for 2 Nos Auto Transformer) | NOS |  | 2
27.2 | 132 KV SIDE
27.2.1 | FEEDER CONTROL PANEL(CPF-1M) | NOS |  | 2
27.2.2 | TRANSFORMER CONTROL PANEL(CPL-1M)(2 for 132 KV Side of 220/132/33 KV Auto Tfr ) | NOS |  | 2
27.2.3 | BUSCOUPLER CONTROL PANEL (CPB-1M) | NOS |  | 1
27.2.4 | FEEDER RELAY PANEL(RPF-1M) | NOS |  | 2
27.2.5 | TRANSFORMER RELAY PANEL(RPL-1M), 02 NOS FOR 220/132 KV AUTO TRANSFORMERS ON 132 KV SIDE | NOS |  | 2
27.2.6 | BUSCOUPLER RELAY PANEL (RPB-1M) | NOS |  | 1
27.2.7 | COMMON PANEL (KP-1) | NOS |  | 1
28 | AC & DC SYSTEM
28.1 | AC SYSTEM
28.1.1 | ACDB (HAVING 400A MCCB) AS PER SPECIFICATION (AC DB-1,AC DB-2 WITH B/C) | SET |  | 1
28.2 | DC SYSTEM
28.2.1 | 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C) | SET |  | 1
23 | DISTLED WATER PLANT OF 10 LTR/HR FOR BATTERY BANKS | SET |  | 1
24 | WALKIE TALKIE SET | SET/PAIR |  | 2
25 | PORTABLE ALUMINIUM LADDER EXTENDABLE TYPE OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT INSIDE SWITCH YARD.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 19) | NOS |  | 1
26 | PEDESTAL MOUNTED WHEEL FITTED DERRICK FOR LIFTING/ LOWERING OF MATERIALS UP TO 1.5 TON CAPACITY.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 20) | SET |  | 1
27 | POWER WINCH NEAR STORE SHED FOR HANDLING MATERIALS UPTO 5 TON CAPACITY. | SET |  | 1
28 | MAINTENANCE TESTING EQUIPMENT (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 17 ANNEXURE - II ,INDICATED IN -SCHEDULE OF REQUIREMENTS OF MAINTENANCE EQUIPMENT) | LOT |  | 1
29 | OTHER TOOLS AND PLANTS (T&P's) REQUIREMENT (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 18 ANNEXURE - III ,INDICATED IN SCHEDULE OF REQUIREMENTS OTHER T&P's) | LOT |  | 1
30 | OFFICE FURNITURE (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 18 ANNEXURE - IV ,INDICATED IN SCHEDULE OF REQUIREMENTS OFFICE FURNITURE) & PLACING IN CONTROL ROOM,CONFERENCE ROOM,OFFICE ROOMS,LIBRARY,TESTING LAB,etc. | LOT |  | 1
31 | BEST QUALITY & APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT & BACK SIDE (where doors of the panels are provided) OF ALL PANELS,BOARDS ETC. | LOT |  | 1
TOTAL OF SUBSTATION-2B(F&I) (PART-I)
Note:
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested not to leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value). No rate shall be furnished/obtained after bid opening (Ref clause no 33.4.1 of INB vol-I)
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | Bidder should be quoted including service tax, no service tax shall be paid/reimbursed.
| Date : | (Signature) ……………………………………………
| Place : | ( Name) ………………………………………………
( Designation ) ……………………………………….
(Common Seal) ……………………………………

## Schedule 2A line
ORISSA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2X160 MVA,220/132 Sub-Station along with 132KV Transmission Lines and associated system
At MENDHASAL
Bid Document No. : Sr. G.M-CPC-TENDER-PACKAGE- 61-02 /2012
(Equipment/Materials Price Break-up of Ex-works Prices against PACKAGE 61-02 / 2012 )
PART-II SCHEDULE-2A (FOR LINE)
| DESCRIPTION OF ITEMS | LINE |  |  |  |  | IN INR
Sl. No. | SUPPLY OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNITS | UNIT WEIGHT IN MT(FOR STRUCTURAL MATERIALS) | Quantity for Construction of 132kv line to existing Chandaka-Khurda 132kv line for LILO arrangement(Line length-1.2Kms( |  | TOTAL QUANTITY | Unit Ex-works Price | Total Ex-works Price | Mode of Transaction (Direct or Bought-out item) | Total Taxes & Duties applicable for transaction between bidder and OPTCL and not included in the price at Column(7) [For bought-out items, taxes & duties excluding Octroi/Entry Tax are invariably included in the price quoted at column(7)]
[10 empty] | Excise Duty | Sales Tax | Other Levies (if any)
1 | 2 | 3 | 4 | 4 | 6 | 5 | 6 | 7=5X6 | 8 | 9 | 10 | 11
1 | SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
1.1 | 220 KV D/C-OC type (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.839 MT, HEIGHT: 35.645 mtrs,BASE:10.8 mtrs) | Nos. | 9.839 | 0 | 0 | 0
1.1.1 | OC +15 Extension(Nominal Weight 8.375 MT) | Nos. | 8.375 | 0 | 0 | 0
1.2 | PBTYPE (30 deg ANGLE ) TOWERS (Nominal unit weight 4.973 MT) | Nos. | 4.973 | 2 | 0 | 2
1.2.1 | +3 EXTENSION (Nominal unit weight 1.018 MT) | Nos. | 1.018 | 1 | 0 | 1
1.2.2 | +6 EXTENSION (Nominal unit weight 2.104 MT) | Nos. | 2.104 | 0 | 0 | 0
1.3 | PC TYPE (60 deg ANGLE ) TOWERS (Nominal unit weight 6.214 MT) | Nos. | 6.214 | 6 | 0 | 6
1.3.1 | +3 EXTENSION (Nominal unit weight 1.119 MT) | Nos. | 1.119 | 1 | 0 | 1
1.3.2 | +6 EXTENSION (Nominal unit weight 2.342 MT) | Nos. | 2.342 | 1 | 0 | 1
1.4 | TEMPLATES
1.4.1 | b) PB (Nominal unit weight 0.602 MT) | Nos. | 0.602 | 1 | 0 | 1
1.4.2 | c) PC (Nominal unit weight 0.904 MT) | Nos. | 0.904 | 1 | 0 | 1
1.4.3 | c) OC+15(Nominal weight 2.50MT) | Nos. | 2.5 | 0 | 0 | 0
1.5 | TOTAL WEIGHT OF THE STRUCTURE (including stubs,Templates,Foundation Bolts and nuts etc) | MT |  | 53.22 | 0 | 53.22
1.6 | Weight of G.I Nuts and Bolts | MT |  | 2.67 | 0 | 2.67
2 | Supply of the following tower accessories as per technical specification and as directed by the engineer in charge.
2.1 | EARTHING DEVICE | Nos. |  | 8 | 0 | 8
2.2 | DANGER BOARD | Nos. |  | 8 | 0 | 8
2.3 | NUMBER PLATE | Nos. |  | 8 | 0 | 8
2.4 | PHASE PLATE | Nos. |  | 24 | 0 | 24
2.5 | ANTICLIMBING DEVICE | Nos. |  | 8 | 0 | 8
2.6 | CIRCUIT PLATE | Nos. |  | 16 | 0 | 16
3 | Supply of following POWER CONDUCTORS in the proposed 132 KV /220kV lines with 1.5% provision for sag and wastage as per the technical specification.
3.1 | AAAC Zebra | Kms. |  | 0 | 0 | 0
3.2 | ACSR Panther (1) Multi circuit – 10.355 Kms (2) Double Circuit – 0.632 Km. | Kms. |  | 7.5 | 0 | 7.5
4 | POWER CONDUCTOR ACESSORIES
4.1 | For AAAC ZEBRA
4.1.1 | VIBRATION DAMPER AAAC ZEBRA | Nos. |  | 0 | 0 | 0
4.1.2 | MID SPAN JOINT AAAC ZEBRA | Nos. |  | 0 | 0 | 0
4.1.3 | Repair sleeve for ACSR Zebra | Nos. |  | 0 | 0 | 0
4.2 | For ACSR PANTHER
4.2.1 | P.A Rod for ACSR Panther | Set |  | 0 | 0 | 0
4.2.2 | VIBRATION DAMPER ACSR Panther | Nos. |  | 120 | 0 | 120
4.2.3 | MID SPAN JOINT ACSR Panther | Nos. |  | 5 | 0 | 5
4.2.4 | Repair sleeve for ACSR Panther | Nos. |  | 5 | 0 | 5
5 | Supply of the GI earth wire of size 7/3.15 mm as per the technical specification, with 1.5% provision for Sag & Wastage as per Technical specification. | Kms. |  | 4 | 0 | 4
6 | EARTH CONDUCTOR ACESSORIES
6.1 | VIBRATION DAMPER | Nos. |  | 24 | 0 | 24
6.2 | FLEXIBLE EARTH BOND | Nos. |  | 24 | 0 | 24
6.3 | SUSPENSION CLAMP | Nos. |  | 0 | 0 | 0
6.4 | TENSION CLAMP | Nos. |  | 24 | 0 | 24
6.5 | MID SPAN JOINT | Nos. |  | 2 | 0 | 2
6.6 | U BOLT | Nos. |  | 24 | 0 | 24
7 | Supply of the following Antifog type disc insulators as per the technical specification and as per the instruction of the Engineer in charge.
7.1 | 70 KN Insulator (taking 5% extra towards wastage) | Nos. |  | 115 | 0 | 115
7.2 | 90 KN Insulator (taking 5% extra towards wastage) | Nos. |  | 1135 | 0 | 1135
7.3 | 160 KN Insulator (taking 5% extra towards wastage) | Nos. |  | 0 | 0 | 0
8 | Supply of the following hard ware fittings suitable for following conductors as per the technical specification.
8.1 | For ACSR ZEBRA conductor
8.1.1 | Single tension Hard wares fittings suitable for 160 KN insulator. | Nos. |  | 0 | 0 | 0
8.1.2 | Double tension Hard wares fittings suitable for 160 KN insulator. | Nos. |  | 0 | 0 | 0
8.2 | For ACSR Panther conductor
8.2.1 | Single suspension Hard wares fittings.(AGS type) suitable for 70 KN insulator. | Nos. |  | 12 | 0 | 12
8.2.2 | Single tension Hard wares fittings suitable for 90 KN insulator. | Nos. |  | 84 | 0 | 84
8.2.3 | Double tension Hard wares fittings suitable for 90 KN insulator. | Nos. |  | 12 | 0 | 12
TOTAL OF LINE -2A (PART-II)
Note:
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested not to leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value). No rate shall be furnished/obtained after bid opening (Ref clause no 33.4.1 of INB vol-I)
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | In mode of transaction column please indicate Direct/Bought-Out. For Taxes & Duties on Direct/Bought-out items ref clause 6.0 of SCC (Vol-IA)
| Date : |  |  |  |  | ( Name) ………………………………………………
| Place : |  |  |  |  | ( Designation ) ……………………………………….
(Common Seal) ……………………………………

## Schedule 2B line
ORISSA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2X160 MVA,220/132 Sub-Station along with 132KV Transmission Lines and associated system
At MENDHASAL
Bid Document No. : Sr. G.M-CPC-TENDER-PACKAGE- 61-02 /2012
(Equipment/Materials Price Break-up of Ex-works Prices against PACKAGE 61-02 / 2012 )
PART-II SCHEDULE-2B (FOR LINE)
| DESCRIPTION OF ITEMS | LINE |  |  |  |  | PRICE IN INDIAN RUPEES
Sl. No. | F&I FOR SUPPLY OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNITS | UNIT WEIGHT IN MT(FOR STRUCTURAL MATERIALS) | Quantity for Construction of 132kv line to existing Chandaka-Khurda 132kv line for LILO arrangement(Line length-1.2Kms( |  | TOTAL QUANTITY | Unit F & I Price | Total F & I Price
1 | 2 | 3 |  | 4 | 5 | 5 | 6 | 7=5x6
1 | SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
1.1 | 220 KV D/C-OC type (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.839 MT, HEIGHT: 35.645 mtrs,BASE:10.8 mtrs) | Nos. | 9.839 | 0 | 0 | 0
1.1.1 | OC +15 Extension(Nominal Weight 8.375 MT) | Nos. | 8.375 | 0 | 0 | 0
1.2 | PBTYPE (30 deg ANGLE ) TOWERS (Nominal unit weight 4.973 MT) | Nos. | 4.973 | 2 | 0 | 2
1.2.1 | +3 EXTENSION (Nominal unit weight 1.018 MT) | Nos. | 1.018 | 1 | 0 | 1
1.2.2 | +6 EXTENSION (Nominal unit weight 2.104 MT) | Nos. | 2.104 | 0 | 0 | 0
1.3 | PC TYPE (60 deg ANGLE ) TOWERS (Nominal unit weight 6.214 MT) | Nos. | 6.214 | 6 | 0 | 6
1.3.1 | +3 EXTENSION (Nominal unit weight 1.119 MT) | Nos. | 1.119 | 1 | 0 | 1
1.3.2 | +6 EXTENSION (Nominal unit weight 2.342 MT) | Nos. | 2.342 | 1 | 0 | 1
1.4 | TEMPLATES
1.4.1 | b) PB (Nominal unit weight 0.602 MT) | Nos. | 0.602 | 1 | 0 | 1
1.4.2 | c) PC (Nominal unit weight 0.904 MT) | Nos. | 0.904 | 1 | 0 | 1
1.4.3 | c) OC+15(Nominal weight 2.50MT) | Nos. | 2.5 | 0 | 0 | 0
1.5 | TOTAL WEIGHT OF THE STRUCTURE (including stubs,Templates,Foundation Bolts and nuts etc) | MT |  | 53.22 | 0 | 53.22
1.6 | Weight of G.I Nuts and Bolts | MT |  | 2.67 | 0 | 2.67
2 | Supply of the following tower accessories as per technical specification and as directed by the engineer in charge.
2.1 | EARTHING DEVICE | Nos. |  | 8 | 0 | 8
2.2 | DANGER BOARD | Nos. |  | 8 | 0 | 8
2.3 | NUMBER PLATE | Nos. |  | 8 | 0 | 8
2.4 | PHASE PLATE | Nos. |  | 24 | 0 | 24
2.5 | ANTICLIMBING DEVICE | Nos. |  | 8 | 0 | 8
2.6 | CIRCUIT PLATE | Nos. |  | 16 | 0 | 16
3 | Supply of following POWER CONDUCTORS in the proposed 132 KV /220kV lines with 1.5% provision for sag and wastage as per the technical specification.
3.1 | AAAC Zebra | Kms. |  | 0 | 0 | 0
3.2 | ACSR Panther (1) Multi circuit – 10.355 Kms (2) Double Circuit – 0.632 Km. | Kms. |  | 7.5 | 0 | 7.5
4 | POWER CONDUCTOR ACESSORIES
4.1 | For AAAC ZEBRA
4.1.1 | VIBRATION DAMPER AAAC ZEBRA | Nos. |  | 0 | 0 | 0
4.1.2 | MID SPAN JOINT AAAC ZEBRA | Nos. |  | 0 | 0 | 0
4.1.3 | Repair sleeve for ACSR Zebra | Nos. |  | 0 | 0 | 0
4.2 | For ACSR PANTHER
4.2.1 | P.A Rod for ACSR Panther | Set |  | 0 | 0 | 0
4.2.2 | VIBRATION DAMPER ACSR Panther | Nos. |  | 120 | 0 | 120
4.2.3 | MID SPAN JOINT ACSR Panther | Nos. |  | 5 | 0 | 5
4.2.4 | Repair sleeve for ACSR Panther | Nos. |  | 5 | 0 | 5
5 | Supply of the GI earth wire of size 7/3.15 mm as per the technical specification, with 1.5% provision for Sag & Wastage as per Technical specification. | Kms. |  | 4 | 0 | 4
6 | EARTH CONDUCTOR ACESSORIES
6.1 | VIBRATION DAMPER | Nos. |  | 24 | 0 | 24
6.2 | FLEXIBLE EARTH BOND | Nos. |  | 24 | 0 | 24
6.3 | SUSPENSION CLAMP | Nos. |  | 0 | 0 | 0
6.4 | TENSION CLAMP | Nos. |  | 24 | 0 | 24
6.5 | MID SPAN JOINT | Nos. |  | 2 | 0 | 2
6.6 | U BOLT | Nos. |  | 24 | 0 | 24
7 | Supply of the following Antifog type disc insulators as per the technical specification and as per the instruction of the Engineer in charge.
7.1 | 70 KN Insulator (taking 5% extra towards wastage) | Nos. |  | 115 | 0 | 115
7.2 | 90 KN Insulator (taking 5% extra towards wastage) | Nos. |  | 1135 | 0 | 1135
7.3 | 160 KN Insulator (taking 5% extra towards wastage) | Nos. |  | 0 | 0 | 0
8 | Supply of the following hard ware fittings suitable for following conductors as per the technical specification.
8.1 | For ACSR ZEBRA conductor
8.1.1 | Single tension Hard wares fittings suitable for 160 KN insulator. | Nos. |  | 0 | 0 | 0
8.1.2 | Double tension Hard wares fittings suitable for 160 KN insulator. | Nos. |  | 0 | 0 | 0
8.2 | For ACSR Panther conductor
8.2.1 | Single suspension Hard wares fittings.(AGS type) suitable for 70 KN insulator. | Nos. |  | 12 | 0 | 12
8.2.2 | Single tension Hard wares fittings suitable for 90 KN insulator. | Nos. |  | 84 | 0 | 84
8.2.3 | Double tension Hard wares fittings suitable for 90 KN insulator. | Nos. |  | 12 | 0 | 12
TOTAL OF LINE -2B (PART-II)
Note:
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested not to leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value). No rate shall be furnished/obtained after bid opening (Ref clause no 33.4.1 of INB vol-I)
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | Bidder should be quoted including service tax, no service tax shall be paid/reimbursed.
| Date : |  |  |  |  | ( Name) ………………
| Place : |  |  |  |  | ( Designation ) ………………
(Common Seal) ……………

## Schedule 2C line
ORISSA POWER TRANSMISSION CORPORATION LIMITED
Construction of 2X160 MVA,220/132 Sub-Station along with 132KV Transmission Lines and associated system
At MENDHASAL
Bid Document No. : Sr. G.M-CPC-TENDER-PACKAGE- 61-02 /2012
(Equipment/Materials Price Break-up of Ex-works Prices against PACKAGE 61-02 / 2012 )
PART-II, SCHEDULE-2C (FOR LINE)
S. No. | DESCRIPTION OF ITEMS | LINE |  |  |  |  | PRICE IN INDIAN RUPEES
|  | UNITS | UNIT WEIGHT IN MT(FOR STRUCTURAL MATERIALS) | 1.2 Kms. OF 220Kv LILO ON 220kV NARENDRAPUR-CHANDAKA TO KARADAGADIA | 11Kms. OF 132kV MULTICIRCUIT Line ON MULTI CIRCUIT TOWERS FROM 132kv S/S KHURDA TO KARADAGADIA |  | Erection Charges
| ERECTION, TESTING AND COMMISSIONING OF FOLLOWING EQUIPMENTS (Complete as per Technical Specification) AND ASSOCIATED CIVIL WORKS AS DETAILED BELOW |  | UNIT WEIGHT IN MT(FOR STRUCTURAL MATERIALS) | Quantity for Construction of 132kv line to existing Chandaka-Khurda 132kv line for LILO arrangement(Line length-1.2Kms( |  | TOTAL QUANTITY | Unit Erection Charges | Total Erection Charges
1 | 2 | 3 | 4 | 4 | 5 | 5 | 6 | 7=5x6
A | ELECTRICAL WORKS
1.1 | 220 KV D/C-OC type (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.839 MT, HEIGHT: 35.645 mtrs,BASE:10.8 mtrs) | Nos. | 9.839 | 0 | 0 | 0
1.1.1 | OC +15 Extension(Nominal Weight 8.375 MT) | Nos. | 8.375 | 0 | 0 | 0
1.2 | PBTYPE (30 deg ANGLE ) TOWERS (Nominal unit weight 4.973 MT) | Nos. | 4.973 | 2 | 0 | 2
1.2.1 | +3 EXTENSION (Nominal unit weight 1.018 MT) | Nos. | 1.018 | 1 | 0 | 1
1.2.2 | +6 EXTENSION (Nominal unit weight 2.104 MT) | Nos. | 2.104 | 0 | 0 | 0
1.3 | PC TYPE (60 deg ANGLE ) TOWERS (Nominal unit weight 6.214 MT) | Nos. | 6.214 | 6 | 0 | 6
1.3.1 | +3 EXTENSION (Nominal unit weight 1.119 MT) | Nos. | 1.119 | 1 | 0 | 1
1.3.2 | +6 EXTENSION (Nominal unit weight 2.342 MT) | Nos. | 2.342 | 1 | 0 | 1
1.4 | TEMPLATES
1.4.1 | b) PB (Nominal unit weight 0.602 MT) | Nos. | 0.602 | 1 | 0 | 1
1.4.2 | c) PC (Nominal unit weight 0.904 MT) | Nos. | 0.904 | 1 | 0 | 1
1.4.3 | c) OC+15(Nominal weight 2.50MT) | Nos. | 2.5 | 0 | 0 | 0
1.5 | TOTAL WEIGHT OF THE STRUCTURE (including stubs,Templates,Foundation Bolts and nuts etc) | MT |  | 53.22 | 0 | 53.22
1.6 | Weight of G.I Nuts and Bolts | MT |  | 2.67 | 0 | 2.67
2 | Erection of the following tower accessories as per technical specification and as directed by the engineer in charge.
2.1 | EARTHING DEVICE | Nos. |  | 8 | 0 | 8
2.2 | DANGER BOARD | Nos. |  | 8 | 0 | 8
2.3 | NUMBER PLATE | Nos. |  | 8 | 0 | 8
2.4 | PHASE PLATE | Nos. |  | 24 | 0 | 24
2.5 | ANTICLIMBING DEVICE | Nos. |  | 8 | 0 | 8
2.6 | CIRCUIT PLATE | Nos. |  | 16 | 0 | 16
3 | Erection of following POWER CONDUCTORS in the proposed 132 KV /220kV lines with 1.5% provision for sag and wastage as per the technical specification.
3.1 | AAAC Zebra | Kms. |  | 0 | 0 | 0
3.2 | ACSR Panther (1) Multi circuit – 10.355 Kms (2) Double Circuit – 0.632 Km. | Kms. |  | 7.5 | 0 | 7.5
4 | POWER CONDUCTOR ACESSORIES
4.1 | For AAAC ZEBRA
4.1.1 | VIBRATION DAMPER AAAC ZEBRA | Nos. |  | 0 | 0 | 0
4.1.2 | MID SPAN JOINT AAAC ZEBRA | Nos. |  | 0 | 0 | 0
4.1.3 | Repair sleeve for ACSR Zebra | Nos. |  | 0 | 0 | 0
4.2 | For ACSR PANTHER
4.2.1 | P.A Rod for ACSR Panther | Set |  | 0 | 0 | 0
4.2.2 | VIBRATION DAMPER ACSR Panther | Nos. |  | 120 | 0 | 120
4.2.3 | MID SPAN JOINT ACSR Panther | Nos. |  | 5 | 0 | 5
4.2.4 | Repair sleeve for ACSR Panther | Nos. |  | 5 | 0 | 5
5 | Erection of the GI earth wire of size 7/3.15 mm as per the technical specification, with 1.5% provision for Sag & Wastage as per Technical specification. | Kms. |  | 4 | 0 | 4
6 | EARTH CONDUCTOR ACESSORIES
6.1 | VIBRATION DAMPER | Nos. |  | 24 | 0 | 24
6.2 | FLEXIBLE EARTH BOND | Nos. |  | 24 | 0 | 24
6.3 | SUSPENSION CLAMP | Nos. |  | 0 | 0 | 0
6.4 | TENSION CLAMP | Nos. |  | 24 | 0 | 24
6.5 | MID SPAN JOINT | Nos. |  | 2 | 0 | 2
6.6 | U BOLT | Nos. |  | 24 | 0 | 24
7 | Erection of the following Antifog type disc insulators as per the technical specification and as per the instruction of the Engineer in charge.
7.1 | 70 KN Insulator (taking 5% extra towards wastage) | Nos. |  | 115 | 0 | 115
7.2 | 90 KN Insulator (taking 5% extra towards wastage) | Nos. |  | 1135 | 0 | 1135
7.3 | 160 KN Insulator (taking 5% extra towards wastage) | Nos. |  | 0 | 0 | 0
8 | Erection of the following hard ware fittings suitable for following conductors as per the technical specification.
8.1 | For ACSR ZEBRA conductor
8.1.1 | Single tension Hard wares fittings suitable for 160 KN insulator. | Nos. |  | 0 | 0 | 0
8.1.2 | Double tension Hard wares fittings suitable for 160 KN insulator. | Nos. |  | 0 | 0 | 0
8.2 | For ACSR Panther conductor
8.2.1 | Single suspension Hard wares fittings.(AGS type) suitable for 70 KN insulator. | Nos. |  | 12 | 0 | 12
8.2.2 | Single tension Hard wares fittings suitable for 90 KN insulator. | Nos. |  | 84 | 0 | 84
8.2.3 | Double tension Hard wares fittings suitable for 90 KN insulator. | Nos. |  | 12 | 0 | 12
9 | TOTAL (Part-A) (ELECTRICAL WORKS)
B | CIVIL WORKS
1 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge.
1.1 | Excavation in all type soil and rocks and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/murrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required.
1.1.1 | Normal soil/compact soil | CUM |  | 110 | 0 | 110
1.1.2 | Dense compact soil | CUM |  | 170 | 0 | 170
1.1.3 | Soft rock | CUM |  | 680 | 0 | 680
1.1.4 | Hard Rock without Blasting | CUM |  | 525 | 0 | 525
1.1.5 | Hard Rock required blasting/using rock breaking machine. | CUM |  | 50 |  | 50
1.2 | Cement Cocreting works(RCC & PCC) as per Technical specification and Direction of the Engineer in charge.
1.2.1 | Design, Engineering and laying of reinforced cement concrete (RCC 1:1.5:3) of grade M20 for open cast foundation with supply of approved quality coarse aggregates(Nominal size 12mm to 20mm) ,fine aggregates, cement and steel of different size(as per design) with cutting, bending, binding with supply of binding wire & positioning in tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, curing,shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM |  | 175 | 0 | 175
1.2.2 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM |  | 11 | 0 | 11
1.3 | REVETMENT:(including Benching)Supply of all materials like cement, random rubles stone ( stone masonry) all type aggregates,labours,Mixture machine,fuel,lubricant & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per the direction of Engineer in charge.
1.3.1 | Excavation in all type of soil including rock & back filling including supply of sand with back filling. | CUM |  | 10 | 0 | 10
1.3.2 | PCC in the ratio1:3:6 including supply of sand 12-20 mm chips. | CUM |  | 4 | 0 | 4
1.3.3 | PCC in the ratio 1:2:4 as above. | CUM |  | 3 | 0 | 3
1.3.4 | RR Masonary work in the ratio 1:5. | CUM |  | 20 | 0 | 20
1.4 | Supply & painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping(both leg & bracing members) | Nos. |  | 10 | 0 | 10
1.5 | Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine optd.), application of required zinc rich paints around the welding portion (two coats),fuel,lubricants,T&P and labours. | Nos. |  | 17000 | 0 | 17000
2 | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting.
2.1 | Preliminary survey, Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | Kms. |  | 1.2 | 0 | 1.2
2.2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | Kms. |  | 1.2 | 0 | 1.2
2.3 | Preparation of land schedule on revenue (if required)maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 132 KV line. Final route to be plotted on 1:50000 topo sheet for approval. | LS |  | 1 | 0 | 1
2.4 | PTCC approval has to be obtained by submitting the required documents to the concerned department through OPTCL. The documents for PTCC clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | LS |  | 1 | 0 | 1
TOTAL (Part-B) (CIVIL WORKS)
TOTAL OF ERECTION WORK LINE – 2C(PART-I) (PART A + PART B)
Note:
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested not to leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value). No rate shall be furnished/obtained after bid opening (Ref clause no 33.4.1 of INB vol-I) .
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | Bidder has to quote rates excluding service tax (if any), service tax shall be paid/reimbursed as per conditions of Bid Document.
Date : | [5 empty] | (Signature) ……………………………………………
Place : | [5 empty] | ( Name) ………………………………………………
( Designation ) ……………………………………….
(Common Seal) ……………………………………

## Schedule_3_Mandatory_
Orissa Power Transmission Corporation Ltd.
Construction of 2X160 MVA,220/132 Sub-Station along with 132KV Transmission Lines and associated system
AT MENDHASAL
Bid Document No. : Sr. G.M-CPC-TENDER-2X160 MVA,220/132 KV SYSTEM MENDHASAL-64 /2011
(Equipment/Materials Price Break-up of Ex-works Prices against MENDHASAL PACKAGE)
(Item wise Price of Mandatory Spares for Package)
SCHEDULE-3, MANDATORY SPARES
Sl. No. | SUPPLY OF MANDATORY SPARES FOR THE FOLLOWING EQUIPMENTS. (As per Technical Specification) | Unit | Quantity for 2X160 MVA,220/132 Substation at MENDHASAL [02 Nos 220 KV TRANSFORMER Bays,7 Nos(2Fdr+2T+1B/C+2 SPARE)132 KV Bays. | Unit Ex-works (Rs.) | Total Ex-works (Rs.) | Mode of Transaction/ (Bought out/Direct) | Excise Duty (Rs.) | Sales Tax/VAT (Rs.) | Other levies (if any) | Unit (F&I) | Total (F&I)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | 245 KV,1600A,40KA,ISOLATORS
1.1 | MALE & FEMALE CONTACTS | SET | 1
1.2 | POWER CONTACTOR,RELAYS,MCBs, SWITCHES,FUSES,PUSH BUTTONS,RESISTORS ETC AS PER APPROVED SCHEMATIC. | SET | 1
1.3 | LIMIT SWITCH | SET | 2
1.4 | MOTOR WITH GEAR ASSEMBLY & BEVEL GEAR ASSEMBLY COMPLETE. | SET | 1
1.5 | AUXILIARY SWITCH CONTACTS ASSEMBLY | SET | 1
1.6 | EARTHING ROD & BLADE CONTACT SIDE | SET | 1
1.7 | HINGE PINS,TERMINAL CONNECTOR,TERMINAL PAD | SET | 1
2 | 245KV,3150A,40KA,SF6,CIRCUIT BREAKER
2.1 | COMPLETE ONE POLE ASSEMBLY OF BREAKER | NOS | 1
2.2 | SPRING CHARGING/PNEUMATIC MOTOR | NOS | 1
2.3 | BREKER AUXILIARY CONTACTS | SET | 1
2.4 | POWER CONTACTORS,RELAYS,MCBs, SWITCHES,FUSES,PUSH BUTTONS,RESISTORS,PRESSURE SWITCHES,LIMIT SWITCHES, ETC AS PER APPROVED SCHEMATIC. | SET | 1
2.5 | DENSITY MONITORING SYSTEM | SET | 1
2.6 | CLOSING COIL | NOS | 4
2.7 | TRIPPING COIL | NOS | 4
2.8 | SF6 GAS FILLING DEVICE | NOS | 1
2.9 | SET OF GASKETS ,"O" RINGS,SEALS PER CIRCUIT BREAKER | SET | 1
3 | 216 KV,METAL OXIDE, 10 KA, CLASS III SURGE ARRESTOR COMPLETE WITH INSULATING BASE & SURGE MONITOR | NOS | 1
4 | 220 KV Bus Post Insulators | NOS | 2
5 | 145 KV,(Different Ratio),31.5KA,4CORE SINGLE PHASE CURRENT TRANSFORMER INCLUDING TERMINAL CONNECTOR | NOS | 1
6 | 145 KV,1200A,40 KA,ISOLATORS
6.1 | MALE & FEMALE CONTACTS | SET | 1
6.2 | POWER CONTACTOR,RELAYS,MCBs, SWITCHES,FUSES,PUSH BUTTONS,RESISTORS ETC AS PER APPROVED SCHEMATIC. | SET | 1
6.3 | LIMIT SWITCH | SET | 2
6.4 | MOTOR WITH GEAR ASSEMBLY & BEVEL GEAR ASSEMBLY COMPLETE. | SET | 1
6.5 | AUXILIARY SWITCH CONTACTS ASSEMBLY | SET | 1
6.6 | EARTHING ROD & BLADE CONTACT SIDE | SET | 1
6.7 | HINGE PINS,TERMINAL CONNECTOR,TERMINAL PAD | SET | 1
7 | 145 KV,6000pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER INCLUDING TERMINAL CONNECTOR | NOS | 1
8 | 120 KV,METAL OXIDE, 10 KA CLASS III SURGE ARRESTOR COMPLETING WITH INSULATING BASE & SURGE MONITOR. | NOS | 2
9 | 145 KV ,2 CORE,SINGLE PHASE,IVT INCLUDING TERMINAL CONNECTOR | NOS | 1
10 | 132 KV Bus Post Insulators | NOS | 3
11 | 145KV,3150A,40 KA,SF6,CIRCUIT BREAKER | NOS
11.1 | COMPLETE ONE POLE ASSEMBLY OF BREAKER | NOS | 1
11.2 | SPRING CHARGING MOTOR | NOS | 1
11.3 | BREKER AUXILIARY CONTACTS | SET | 1
11.4 | POWER CONTACTORS,RELAYS,MCBs, SWITCHES,FUSES,PUSH BUTTONS,RESISTORS,PRESSURE SWITCHES,LIMIT SWITCHES, ETC AS PER APPROVED SCHEMATIC. | SET | 1
11.5 | DENSITY MONITORING SYSTEM | SET | 1
11.6 | CLOSING COIL | NOS | 4
11.7 | TRIPPING COIL | NOS | 4
11.8 | SF6 GAS FILLING DEVICE | NOS | 1
11.9 | SET OF GASKETS ,"O" RINGS,SEALS PER CIRCUIT BREAKER | SET | 1
12 | BUS BAR & CIRCUIT MATERIALS | LOT
12.1 | 160 kN INSULATOR STRINGS for twin Moose cond ( TENSION)-220 KV | SET | 2
12.2 | 160 kN INSULATOR STRINGS for single Moose cond (TENSION)-220 KV | SET | 2
12.3 | 120 kN INSULATOR STRINGS for Double Moose cond (TENSION)-132 KV | SET | 2
12.4 | 120 kN INSULATOR STRINGS for Single Moose cond( TENSION)-132 KV | SET | 2
12.5 | 120 kN INSULATOR STRINGS for Double Moose cond ( TENSION)-33 KV | SET | 2
12.6 | 120 kN INSULATOR STRINGS for Single Moose cond(TENSION)-33 KV | SET | 2
12.7 | 90 kN INSULATOR STRINGS for Double/ Single Moose cond ( SUSPENSION)-220 KV | SET | 2
12.8 | 90 kN INSULATOR STRINGS for Double/ Single Moose cond ( SUSPENSION)-132 KV | SET | 2
12.9 | 90 kN INSULATOR STRINGS for Double/ Single Moose cond (SUSPENSION)-33 KV | SET | 2
13 | ACSR MOOSE CONDUCTOR | MTRS | 500
14 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | SET (EACH TYPE THREE NOS.) | 1
15 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
15.1 | POWER CABLES,1.1KV,XLPE,ARMOURED, ALUMINIUM CONDUCTOR(As per Specification)
15.1.1 | 3.5 CX120 mm2 (ONE PIECE OF MAXM. LENGTH OF CABLE USED) | PCS. | 1
15.1.2 | 3.5 CX70 mm2 (ONE PIECE OF MAXM. LENGTH OF CABLE USED) | PCS. | 1
15.1.3 | 3.5 CX35 mm2 (ONE PIECE OF MAXM. LENGTH OF CABLE USED) | PCS. | 1
15.1.4 | 4 CX 16 mm2 | MTRS | 250
15.1.5 | 4 CX 6 mm2 | MTRS | 250
15.1.6 | 2CX 6 mm2 | MTRS | 250
15.2 | CONTROL CABLES,1.1 KV, PVC,STRANDED COPPER(As per specification)
15.2.1 | 4 CX 2.5 mm2 (ONE DRUM HAVING LENGTH OF 500 MTRS) | NOS. | 1
15.2.2 | 5 CX 2.5 mm2 (ONE DRUM HAVING LENGTH OF 500 MTRS) | NOS. | 1
15.2.3 | 7 CX 2.5 mm2 (ONE DRUM HAVING LENGTH OF 500 MTRS) | NOS. | 1
15.2.4 | 10 CX 2.5 mm2 (ONE DRUM HAVING LENGTH OF 500 MTRS) | NOS. | 1
15.2.5 | 12 CX 2.5 mm2 (ONE DRUM HAVING LENGTH OF 250 MTRS) | NOS. | 1
15.2.6 | 16 CX 2.5 mm2 (ONE DRUM HAVING LENGTH OF 250 MTRS) | NOS. | 1
15.2.7 | 19 CX 2.5 mm2 (ONE DRUM HAVING LENGTH OF 250 MTRS) | NOS. | 1
15.3 | CARRIER COMMUNICATION & OTHER MATERIALS
15.3.1 | 132 KV,800 A,0.5mH,Pedestal Mounting WAVE TRAP | NOS | 1
15.3.2 | LINE MATCHING UNIT & LINE MATCHING DISTRIBUTION UNIT | SET | 1
16 | PROTECTION,CONTROL METERING,EVENT LOGGER,BUS BAR PROTN PAN,COMM PAN,RELAY TOOL KITS AS PER TECH SPEC AND BOQ FOR PCM
16.1 | 220 KV SIDE
16.1.1 | OVER CURRENT & EARTH FAULT RELAY | NOS | 1
16.1.2 | MASTER TRIP RELAY | NOS | 1
16.1.3 | DIFFERENTIAL PROTECTION RELAY | NOS | 1
16.1.4 | TRIP SUPERVISION RELAY | NOS | 2
16.1.5 | OTHER AUXILIARY RELAYS(EACH 1 NO. OF DIFFERENT TYPE) | SET | 1
16.1.6 | ANNUNCIATOR | NOS | 2
16.1.7 | DISCREPANCY CONTROL SWITCH
16.1.8 | a) FOR CIRCUIT BREAKER | NOS | 2
16.1.9 | b) FOR ISOLATOR | NOS | 2
16.1.10 | PROTECTION TRANSFER SWITCH | NOS | 1
16.1.11 | AMMETER SELECTOR SWITCH | NOS | 2
16.1.12 | VOLTMETER SELECTOR SWITCH | NOS | 2
16.1.13 | AMMETER ALONG WITH TRANSDUCER | SET | 1
16.1.14 | VOLTMETER ALONG WITH TRANSDUCER | SET | 1
16.1.15 | MW METER ALONG WITH TRANSDUCER | SET | 1
16.1.16 | MVAR METER ALONG WITH TRANSDUCER | SET | 1
16.2 | 132 KV SIDE
16.2.1 | DISTANCE PROTECTION RELAY | NOS | 1
16.2.2 | OVER CURRENT & EARTH FAULT RELAY | NOS | 1
16.2.3 | MASTER TRIP RELAY | NOS | 1
16.2.4 | TRIP SUPERVISION RELAY | NOS | 2
16.2.5 | OTHER AUXILIARY RELAYS(EACH 1 NO. OF DIFFERENT TYPE) | SET | 1
16.2.6 | ANNUNCIATOR | NOS | 2
16.2.7 | DISCREPANCY CONTROL SWITCH
16.2.8 | a) FOR CIRCUIT BREAKER | NOS | 2
16.2.9 | b) FOR ISOLATOR | NOS | 2
16.2.10 | PROTECTION TRANSFER SWITCH | NOS | 1
16.2.11 | AMMETER SELECTOR SWITCH | NOS | 1
16.2.12 | VOLTMETER SELECTOR SWITCH | NOS | 1
16.2.13 | AMMETER ALONG WITH TRANSDUCER | SET | 1
16.2.14 | VOLTMETER ALONG WITH TRANSDUCER | SET | 1
16.2.15 | MW METER ALONG WITH TRANSDUCER | SET | 1
16.2.16 | MVAR METER ALONG WITH TRANSDUCER | SET | 1
TOTAL OF SCHEDULE-3
Note:
1 | Before filling up rate/amount etc. in the schedules bidders are requested to read carefully the instruction given in Vol-I of Bidding Document.
2 | Bidders are required to fill up amount in all column except shaded portion.
3 | Bidders are requested to not leave any column blank. If any column is left blank it shall be considered that amount against those items are included in any other item and the total amount for that item shall be calculated as free of cost (Zero value).
4 | Kindly enclose soft copy of the duly filled schedule in a CD with the priced copy of Bid.
5 | In mode of transaction column please indicate Direct/Bought-Out. For Taxes & Duties on Direct/Bought-out items ref clause 6.0 of SCC (Vol-IA)
6 | Bidder should quoted F&I including service tax, no service tax shall be paid/reimbursed on this account.
Date : | [7 empty] | (Signature)…………………………………..
Place: | [7 empty] | (Printed Name)……………………………..
(Designation)………………………….........
(Common Seal)…………………………….